## Boulder Bay
BOULDER BAY WASTEWATER TREATMENT WORKS - ANNUAL POLLUTION MONITORING SUMMARY - 2022-2023
| Environment Protection Licence No. 358 |  |  | Licensee | Hunter Water Corporation
| Date Obtained: 6 July 2023 |  |  |  | 36 Honeysuckle Drive
| Date Published: 6 March 2024 |  |  |  | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 | Site Description - Outfall Distribution Chamber
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 July 2022 to 30 June 2023
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM * | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Number of measurements | Actual | Limit | Actual | Limits
Aldrin | micrograms per litre | 2 times a year | 2 | <0.01 | <0.01 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
alpha-BHC | micrograms per litre | 2 times a year | 2 | <0.01 | <0.01 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Arsenic | micrograms per litre | 2 times a year | 2 | 0.4 | 0.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
beta-BHC | micrograms per litre | 2 times a year | 2 | <0.01 | <0.01 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Biochemical Oxygen Demand | milligrams per litre | Every 12 days exactly | 31 | <2 | 7 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Cadmium | micrograms per litre | 2 times a year | 2 | <0.05 | <0.2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Chlordane, total | micrograms per litre | 2 times a year | 2 | <0.01 | <0.01 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Chromium | micrograms per litre | 2 times a year | 2 | 0.3 | 0.6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Copper | micrograms per litre | 2 times a year | 2 | 1 | 2.6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Dieldrin | micrograms per litre | 2 times a year | 2 | <0.01 | <0.01 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Endosulfan | micrograms per litre | 2 times a year | 2 | <0.01 | <0.01 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Endrin | micrograms per litre | 2 times a year | 2 | <0.01 | <0.01 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
gamma-BHC (Lindane) | micrograms per litre | 2 times a year | 2 | <0.01 | <0.01 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Heptachlor | micrograms per litre | 2 times a year | 2 | <0.005 | <0.005 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Heptachlor epoxide | micrograms per litre | 2 times a year | 2 | <0.01 | <0.01 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Hexachlorobenzene | micrograms per litre | 2 times a year | 2 | <0.01 | <0.01 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Lead | micrograms per litre | 2 times a year | 2 | <0.1 | <0.2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Mercury | micrograms per litre | 2 times a year | 2 | <0.1 | <0.1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Methoxychlor | micrograms per litre | 2 times a year | 2 | <0.01 | <0.01 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nickel | micrograms per litre | 2 times a year | 2 | 1.1 | 2.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Oil and Grease | milligrams per litre | Every 12 days exactly | 31 | <1 | 2 | 5 | <2 | 10 | <2 | 15 | 0 * | - | N/A | N/A | Yes
p,p-DDD | micrograms per litre | 2 times a year | 2 | <0.01 | <0.01 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
p,p-DDE | micrograms per litre | 2 times a year | 2 | <0.01 | <0.01 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
p,p-DDT | micrograms per litre | 2 times a year | 2 | <0.01 | <0.01 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Polychlorinated biphenyls | micrograms per litre | 2 times a year | 2 | <0.1 | <0.1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Selenium | micrograms per litre | 2 times a year | 2 | <0.2 | <0.2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Silver | micrograms per litre | 2 times a year | 2 | <0.1 | <1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | Every 12 days exactly | 31 | <1 | 28 | 35 | 3 | 50 | 10 | 60 | 0 * | - | N/A | N/A | Yes
Zinc | micrograms per litre | 2 times a year | 2 | 23 | 36 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
*No 3DGM calculations were required during the 2022-23 Annual Return Period
VOLUME MONITORING
Annual Summary
1 July 2022 to 30 June 2023
Monitoring Point |  | Unit of | Sampling | No. of times measured during the year |  |  |  |  | Volume | Within
|  | Measurement | Frequency |  |  | Minimum | Mean | Maximum | Limit | Limits?
Point 1 - Outfall Distribution Chamber |  | kilolitres per day | Daily | 365 |  | 3440 | 9709 | 23220 | 80000 | Yes
Point 2 - Inlet Channel |  | kilolitres per day | Daily | 365 |  | 3440 | 9709 | 23180 | N/A | N/A
Point 3 - Bypass Channel |  | kilolitres per day | Daily | 365 |  | 0 | 1 | 270 | N/A | N/A
Note on E27: jloader: <0.01
Note on E29: jloader: <0.01
Note on F29: jloader: <0.01
Note on F30: jloader: <0.01