## Branxton
BRANXTON WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - MARCH 2022
|  | Environment Protection Licence No. 1680 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 4 April 2022 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 22 April 2022 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 |  | Site Description - Outlet to Farmers Reuse Storage
Site Code 5SL0500
[6 empty] | No. of times measured during the month for licence reporting * | Monthly Summary
1 March 2022 to 31 March 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Chlorine (total residual) | Total Chlorine | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Enterococci | Enterococci | colony forming units per 100 mL |  | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | 2nd pH-S1 | colony forming units per 100 mL | (cfu/100ml) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrate+nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Kjeldahl Nitrogen | TKN | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | 6.5 - 8.5 | - - - | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS(b) | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
* No samples were collected as no discharge occurred during the month
EPA Id. No. 11 |  | Site Description - Discharge to Black Creek from Reuse Water Storage
Site Code 5BL0500
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 March 2022 to 31 March 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Chlorophyll 'a' | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Chlorine (total residual) | Reported TC | milligrams per litre | (mg/L) | First 24hrs then weekly | WEEKLY | 4 | <0.1 | <0.1 | <0.1 | <0.1 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 12 |  | Site Description - Reuse Water Pump Station
Site Code 5SK0535
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 March 2022 to 31 March 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | <2 | 2.4 | <2 | 3 | N/A | N/A | N/A | N/A | N/A
Enterococci | Enterococci | colony forming units per 100 mL |  | Weekly | WEEKLY | 5 | <1 | 1.2 | <1 | 2 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL | (cfu/100ml) | Weekly | WEEKLY | 5 | <1 | 1.4 | ~<1 | 3 | N/A | N/A | N/A | N/A | N/A
Nitrate+nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Monthly | MONTHLY | 5 | 2.61 | 3.792 | 3.58 | 5.37 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Monthly | MONTHLY | 5 | <0.05 | 0.066 | 0.05 | 0.11 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Monthly | MONTHLY | 5 | 3.31 | 4.972 | 4.56 | 7.47 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly | WEEKLY | 5 | 7.06 | 7.202 | 7.17 | 7.36 | N/A | N/A | 6.5 - 8.5 | 7.06 - 7.36 | Yes
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Monthly | MONTHLY | 5 | 0.096 | 0.1356 | 0.12 | 0.181 | N/A | N/A | N/A | N/A | N/A
Total Kjeldahl Nitrogen | TKN | milligrams per litre | (mg/L) | Monthly | MONTHLY | 5 | 0.7 | 1.18 | 0.9 | 2.1 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | <1 | <1 | <1 | 1 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 13 |  | Site Description - Outlet to Anvil Creek from Wet Weather Storage Pond.
Site Code 5OV0500
[6 empty] | No. of times measured during the month for licence reporting ** | Monthly Summary
1 March 2022 to 31 March 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | First 24hrs then weekly |  | 2 | 6 | 7 | 7 | 7 | N/A | N/A | N/A | N/A | N/A
Enterococci | Enterococci | colony forming units per 100 mL |  | First 24hrs then weekly |  | 2 | 930 | 2415 | 2415 | 3900 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | (cfu/100ml) | First 24hrs then weekly |  | 2 | 31000 | 64500 | 64500 | 98000 | N/A | N/A | N/A | N/A | N/A
Nitrate+nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | First 24hrs then weekly |  | 2 | 1.1 | 2.1 | 2.1 | 3.13 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | First 24hrs then weekly |  | 2 | 4.75 | 4.89 | 4.89 | 5.03 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | First 24hrs then weekly |  | 2 | 7.05 | 7.15 | 7.15 | 7.24 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | First 24hrs then weekly |  | 2 | 1.21 | 1.25 | 1.25 | 1.29 | N/A | N/A | N/A | N/A | N/A
Total Kjeldahl Nitrogen | TKN | milligrams per litre | (mg/L) | First 24hrs then weekly |  | 2 | 8.5 | 8.6 | 8.6 | 8.7 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS(b) | milligrams per litre | (mg/L) | First 24hrs then weekly |  | 2 | 24 | 39 | 39 | 53 | N/A | N/A | N/A | N/A | N/A
** Two overflow events occurred during March 2022, with one sample occurring outside the required 24 hour sampling frequency
Note: For pollutants with less than four samples measured during the monthly period see below for interpretation of summary tables: One required sample for licence reporting: Min, Mean, Median and Max values are all the exact data point Two required samples for licence reporting: Min and Max values are the two exact data points Three required samples for licence reporting: Min, Median and Max values are the three exact data points
VOLUME MONITORING |  |  | 90
Monthly Summary
1 March 2022 to 31 March 2022
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
|  |  |  | Measurement |  | Frequency | [5 empty] | Limit
Point 1 - Anvil Creek Discharge |  |  | 5 | kilolitres per day | 0 | Daily | 31 |  | 0 | 0 | 0 | 31104 | Yes
Point 2 - Woodlot Discharge |  |  | 9 | kilolitres per day | 0 | Daily | 31 |  | 0 | 0 | 0 | N/A | N/A
Point 6 - Farmer Discharge |  |  | 10 | kilolitres per day | 0 | Daily | 31 |  | 0 | 0 | 0 | N/A | N/A
Point 8 - Spillway to Anvil from Wet Weather Storage |  |  | 14 | kilolitres per day | 0 | Daily | 31 |  | 0 | 0 | 0 | N/A | N/A
Point 9 - Spillway to Anvil from Farmer's Storage |  |  | 15 | kilolitres per day | 0 | Daily | 31 |  | 0 | 0 | 0 | N/A | N/A
Point 10 - Vintage Golf Course |  |  | 7 | kilolitres per day | 0 | Daily | 31 |  | 0 | 0 | 0 | N/A | N/A
Point 11 - Black Creek Discharge |  |  | 8 | kilolitres per day | 3726 | Daily | 31 |  | 709 | 3702.2903 | 5574 | 31104 | Yes
Point 13 - Outlet to Anvil from Wet Weather Storage |  |  | 13 | kilolitres per day | 0 | Daily | 31 |  | 0 | 268 | 3243 | N/A | N/A
Point 14 - Branxton Golf Course |  |  | 11 | kilolitres per day | 131.9 | Daily | 31 |  | 0 | 8.9548 | 66.4 | N/A | N/A
Combined Point 1, 8, 9, 11 and 13 |  |  | 16 | kilolitres per day | 3726 | Daily | 31 |  | 709 | 3981.6129 | 8041 | 31104 | Yes
Note on D82: awebb: Last row of flow table