## Burwood Beach
BURWOOD BEACH WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - APRIL 2020
|  | Environment Protection Licence No. 1683 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 7 May 2020 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 21 May 2020 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 |  | Site Description - Inspection pit down stream of the secondary clarifier and the wet weather bypass chamber
Site Code 5SL0600
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 April 2020 to 30 April 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Aldrin | Aldrin | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
alpha-BHC | α-BHC | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Arsenic | As | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
beta-BHC | β-BHC | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Every 12 days exactly | Fortnightly | 2 | 9 | 31.5 | 31.5 | 54 | N/A | N/A | N/A | N/A | N/A
Cadmium | Cd | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Chlordane, total | Chlordane | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Chromium | Cr | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Copper | Cu | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Dieldrin | Dieldrin | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Endosulfan | Endosulphan | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Endrin | Endrin | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
gamma-BHC (Lindane) | Lindane | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Heptachlor | Heptachlor | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Heptachlor epoxide | Heptachlor epoxide | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Hexachlorobenzene | HCB | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Lead | Pb | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Mercury | Hg | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Methoxychlor | Methoxychlor | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nickel | Ni | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Every 12 days exactly | Fortnightly | 2 | <2 | 3 | 3 | 4 | 15 | -* | N/A | N/A | Yes
p,p-DDD | DDD | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
p,p-DDE | DDE | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
p,p-DDT | DDT | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Polychlorinated biphenyls | PCB | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Selenium | Se | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Silver | Ag | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Every 12 days exactly | Fortnightly | 2 | 5 | 5.5 | 5.5 | 6 | 60 | -* | N/A | N/A | Yes
Zinc | Zn | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
* No 3DGM calculations required by licence this month.
P3
Test
EPA Id. No. 3 |  | Site Description - Sludge pumping station
Site Code 5CB0600
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 April 2020 to 30 April 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Chlorophyll 'a' | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Aldrin | Aldrin | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
alpha-BHC | α-BHC | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
Arsenic | As | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 5 | 20 | 24.46 | 23.7 | 29.9 | N/A | N/A | N/A | N/A | N/A
beta-BHC | β-BHC | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
Cadmium | Cd | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 5 | 2.6 | 3.22 | 3.1 | 4.1 | N/A | N/A | N/A | N/A | N/A
Chlordane, total | Chlordane | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.020 | <0.020 | <0.020 | <0.020 | N/A | N/A | N/A | N/A | N/A
Chromium | Cr | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 5 | 30.7 | 37.8 | 37.7 | 44.4 | N/A | N/A | N/A | N/A | N/A
Copper | Cu | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 5 | 912 | 1087.2 | 1060 | 1400 | N/A | N/A | N/A | N/A | N/A
Dieldrin | Dieldrin | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
Endosulfan | Endosulphan | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
Endrin | Endrin | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
gamma-BHC (Lindane) | Lindane | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
Heptachlor | Heptachlor | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.005 | <0.005 | <0.005 | <0.005 | N/A | N/A | N/A | N/A | N/A
Heptachlor epoxide | Heptachlor epoxide | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
Hexachlorobenzene | HCB | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
Lead | Pb | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 5 | 90.6 | 128.86 | 139 | 173 | N/A | N/A | N/A | N/A | N/A
Mercury | Hg | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 5 | <0.10 | <0.10 | <0.10 | <0.10 | N/A | N/A | N/A | N/A | N/A
Methoxychlor | Methoxychlor | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
Nickel | Ni | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 5 | 40.6 | 54.62 | 52.9 | 79 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Every 6 days exactly | INCLUDE? | 5 | 18.5 | 31.18 | 29.4 | 44.9 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Every 6 days exactly | INCLUDE? | 5 | 9 | 72.2 | 103 | 126 | N/A | N/A | N/A | N/A | N/A
p,p-DDD | DDD | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
p,p-DDE | DDE | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
p,p-DDT | DDT | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
Polychlorinated biphenyls | PCB | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.10 | <0.10 | <0.10 | <0.10 | N/A | N/A | N/A | N/A | N/A
Selenium | Se | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 5 | 9.7 | 11.52 | 10.6 | 15.6 | N/A | N/A | N/A | N/A | N/A
Silver | Ag | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 5 | 6 | 8.2 | 7 | 12 | N/A | N/A | N/A | N/A | N/A
Total Solids | Total Solids | percent by weight | % | Every 6 days exactly | INCLUDE? | 5 | 0.39 | 0.45 | 0.42 | 0.6 | N/A | N/A | N/A | N/A | N/A
Zinc | Zn | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 5 | 2360 | 2978 | 2800 | 4120 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 10 |  | Site Description - Pump well between clarifier and the sludge line
Site Code 5SG0601
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 April 2020 to 30 April 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Chlorophyll 'a' | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Total Solids | Total Solids | percent by weight | % | Every 6 days exactly |  | 5 | <0.10 | 0.106 | <0.10 | 0.13 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 11 |  | Site Description - Scum pump well
Site Code 5CC0600
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 April 2020 to 30 April 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Total Solids | Total Solids | percent by weight | % | Every 6 days exactly |  | 5 | <0.10 | 4.702 | 0.52 | 21.8 | N/A | N/A | N/A | N/A | N/A
VOLUME MONITORING |  |  | 116
Monthly Summary
1 April 2020 to 30 April 2020
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  |  | Volume | Within Limits
|  |  |  | Measurement |  | Frequency |  |  | Maximum | Limit
Point 1 - Ocean Outfall |  |  | 12 | kilolitres per day | 75395.807 | Daily | 30 |  | 75395.807 | 510000 | Yes
Point 3 - Sludge Pumping Station |  |  | 11 | kilolitres per day | 2304.924 | Daily | 30 |  | 2304.924 | 5000 | Yes
Point 10 - Sludge Dilution |  |  | 10 | kilolitres per day | 0 | Daily | 30 |  | 0 | N/A | N/A
Point 11 - Scum Pumping Station |  |  | 15 | kilolitres per day | 48.963 | Daily | 30 |  | 48.963 | N/A | N/A
Point 12 - Total Volume |  |  | 3 | kilolitres per day | 77.6 | Daily | 30 |  | 77600 | N/A | N/A
Point 13 - Treated Volume |  |  | 4 | kilolitres per day | 74.3 | Daily | 30 |  | 74300 | N/A | N/A
Point 17 - Bypass Volume |  |  | 9 | kilolitres per day | 5.5 | Daily | 30 |  | 5500 | N/A | N/A
Note on D105: awebb: Last row of flow table