## Burwood Beach
BURWOOD BEACH WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - OCTOBER 2020
|  | Environment Protection Licence No. 1683 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 9 November 2020 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 19 November 2020 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 |  | Site Description - Inspection pit down stream of the secondary clarifier and the wet weather bypass chamber
Site Code 5SL0600
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 October 2020 to 31 October 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Aldrin | Aldrin | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
alpha-BHC | α-BHC | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Arsenic | As | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
beta-BHC | β-BHC | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Every 12 days exactly | Fortnightly | 3 | 24 | 26.6667 | 28 | 28 | N/A | N/A | N/A | N/A | N/A
Cadmium | Cd | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Chlordane, total | Chlordane | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Chromium | Cr | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Copper | Cu | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Dieldrin | Dieldrin | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Endosulfan | Endosulphan | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Endrin | Endrin | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
gamma-BHC (Lindane) | Lindane | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Heptachlor | Heptachlor | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Heptachlor epoxide | Heptachlor epoxide | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Hexachlorobenzene | HCB | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Lead | Pb | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Mercury | Hg | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Methoxychlor | Methoxychlor | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nickel | Ni | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Every 12 days exactly | Fortnightly | 3 | <2 | <2 | <2 | 2 | 15 | -* | N/A | N/A | Yes
p,p-DDD | DDD | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
p,p-DDE | DDE | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
p,p-DDT | DDT | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Polychlorinated biphenyls | PCB | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Selenium | Se | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Silver | Ag | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Every 12 days exactly | Fortnightly | 3 | 5 | 6.3333 | 6 | 8 | 60 | -* | N/A | N/A | Yes
Zinc | Zn | micrograms per litre | (µg/L) | 2 times a year | Bi-Annual | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
* No 3DGM calculations required by licence this month.
P3
Test
EPA Id. No. 3 |  | Site Description - Sludge pumping station
Site Code 5CB0600
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 October 2020 to 31 October 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Chlorophyll 'a' | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Aldrin | Aldrin | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
alpha-BHC | α-BHC | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
Arsenic | As | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 4 | 17.4 | 19.9 | 18.9 | 24.4 | N/A | N/A | N/A | N/A | N/A
beta-BHC | β-BHC | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
Cadmium | Cd | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 4 | 3 | 3.675 | 3.35 | 5 | N/A | N/A | N/A | N/A | N/A
Chlordane, total | Chlordane | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.020 | <0.020 | <0.020 | <0.020 | N/A | N/A | N/A | N/A | N/A
Chromium | Cr | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 4 | 27.3 | 35.125 | 32.7 | 47.8 | N/A | N/A | N/A | N/A | N/A
Copper | Cu | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 4 | 502 | 956.75 | 952.5 | 1420 | N/A | N/A | N/A | N/A | N/A
Dieldrin | Dieldrin | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
Endosulfan | Endosulphan | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
Endrin | Endrin | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
gamma-BHC (Lindane) | Lindane | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
Heptachlor | Heptachlor | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.005 | <0.005 | <0.005 | <0.005 | N/A | N/A | N/A | N/A | N/A
Heptachlor epoxide | Heptachlor epoxide | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
Hexachlorobenzene | HCB | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
Lead | Pb | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 4 | 105 | 147 | 143 | 197 | N/A | N/A | N/A | N/A | N/A
Mercury | Hg | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 4 | <0.1 | 0.175 | <0.1 | 0.4 | N/A | N/A | N/A | N/A | N/A
Methoxychlor | Methoxychlor | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
Nickel | Ni | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 4 | 24.9 | 37.6 | 39.05 | 47.4 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Every 6 days exactly | INCLUDE? | 6 | 13.8 | 26.7167 | 25.4 | 47.1 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Every 6 days exactly | INCLUDE? | 6 | 23 | 102.6667 | 73 | 306 | N/A | N/A | N/A | N/A | N/A
p,p-DDD | DDD | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
p,p-DDE | DDE | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
p,p-DDT | DDT | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.010 | <0.010 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A
Polychlorinated biphenyls | PCB | micrograms per litre | (µg/L) | Monthly | INCLUDE? | 1 | <0.10 | <0.10 | <0.10 | <0.10 | N/A | N/A | N/A | N/A | N/A
Selenium | Se | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 4 | 5.7 | 8.825 | 9.3 | 11 | N/A | N/A | N/A | N/A | N/A
Silver | Ag | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 4 | 4 | 6.25 | 5.5 | 10 | N/A | N/A | N/A | N/A | N/A
Total Solids | Total Solids | percent by weight | % | Every 6 days exactly | INCLUDE? | 6 | 0.27 | 0.41167 | 0.38 | 0.61 | N/A | N/A | N/A | N/A | N/A
Zinc | Zn | micrograms per litre | (µg/L) | Weekly | INCLUDE? | 4 | 2430 | 3535 | 3475 | 4760 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 10 |  | Site Description - Pump well between clarifier and the sludge line
Site Code 5SG0601
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 October 2020 to 31 October 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Chlorophyll 'a' | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Total Solids | Total Solids | percent by weight | % | Every 6 days exactly |  | 6 | <0.10 | <0.10 | <0.10 | <0.10 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 11 |  | Site Description - Scum pump well
Site Code 5CC0600
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 October 2020 to 31 October 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Total Solids | Total Solids | percent by weight | % | Every 6 days exactly |  | 6 | 0.31 | 1.3417 | 1.575 | 2.18 | N/A | N/A | N/A | N/A | N/A
Note: For pollutants with less than four samples measured during the monthly period see below for interpretation of summary tables: One required sample for licence reporting: Min, Mean, Median and Max values are all the exact data point Two required samples for licence reporting: Min and Max values are the two exact data points Three required samples for licence reporting: Min, Median and Max values are the three exact data points
VOLUME MONITORING |  |  | 116
Monthly Summary
1 October 2020 to 31 October 2020
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
|  |  |  | Measurement |  | Frequency | [5 empty] | Limit
Point 1 - Ocean Outfall |  |  | 12 | kilolitres per day | 369792.974 | Daily | 31 |  | 34135 | 65321 | 369792.974 | 510000 | Yes
Point 3 - Sludge Pumping Station |  |  | 11 | kilolitres per day | 2511.462 | Daily | 31 |  | 671 | 2247 | 2511.462 | 5000 | Yes
Point 10 - Sludge Dilution |  |  | 10 | kilolitres per day | 0 | Daily | 31 |  | 0 | 0 | 0 | N/A | N/A
Point 11 - Scum Pumping Station |  |  | 15 | kilolitres per day | 46.386 | Daily | 31 |  | 0 | 14 | 33 | N/A | N/A
Point 12 - Total Volume |  |  | 3 | kilolitres per day | 96.8 | Daily | 31 |  | 36500 | 67568 | 372200 | N/A | N/A
Point 13 - Treated Volume |  |  | 4 | kilolitres per day | 84 | Daily | 31 |  | 33800 | 54848 | 140700 | N/A | N/A
Point 17 - Bypass Volume |  |  | 9 | kilolitres per day | 12.8 | Daily | 31 |  | 0 | 12810 | 231500 | N/A | N/A
Note on D109: awebb: Last row of flow table