## Burwood Beach
BURWOOD BEACH WASTEWATER TREATMENT WORKS - ANNUAL POLLUTION MONITORING SUMMARY - 2019-2020
| Environment Protection Licence No. 1683 |  |  |  | Hunter Water Corporation
| Date Obtained: 3 July 2020 |  |  |  | 36 Honeysuckle Drive
| Date Published: 20 July 2020 |  |  |  | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 | Site Description - Inspection pit down stream of the secondary clarifier and the wet weather bypass chamber
Site Code 5SL0600
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 July 2019 to 30 June 2020
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Number of measurements | Limit | Actual | Limit | Actual | Limits
Aldrin | micrograms per litre | 2 times a year | 2 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
alpha-BHC | micrograms per litre | 2 times a year | 2 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Arsenic | micrograms per litre | 2 times a year | 2 | 2 | 2.6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
beta-BHC | micrograms per litre | 2 times a year | 2 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Biochemical Oxygen Demand | milligrams per litre | Every 12 days exactly | 30 | 6 | 76 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Cadmium | micrograms per litre | 2 times a year | 2 | <0.20 | <0.20 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Chlordane, total | micrograms per litre | 2 times a year | 2 | <0.020 | <0.020 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Chromium | micrograms per litre | 2 times a year | 2 | 0.9 | 1.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Copper | micrograms per litre | 2 times a year | 2 | 7.3 | 9.2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Dieldrin | micrograms per litre | 2 times a year | 2 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Endosulfan | micrograms per litre | 2 times a year | 2 | <0.030 | <0.030 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Endrin | micrograms per litre | 2 times a year | 2 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
gamma-BHC (Lindane) | micrograms per litre | 2 times a year | 2 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Heptachlor | micrograms per litre | 2 times a year | 2 | <0.005 | <0.005 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Heptachlor epoxide | micrograms per litre | 2 times a year | 2 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Hexachlorobenzene | micrograms per litre | 2 times a year | 2 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Lead | micrograms per litre | 2 times a year | 2 | 0.7 | 1.6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Mercury | micrograms per litre | 2 times a year | 2 | <0.1 | <0.1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Methoxychlor | micrograms per litre | 2 times a year | 2 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nickel | micrograms per litre | 2 times a year | 2 | 4.1 | 4.7 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Oil and Grease | milligrams per litre | Every 12 days exactly | 30 | <2 | 5 | 5 | <2 | 10 | 3 | 0* | 15 | - | N/A | N/A | Yes
p,p-DDD | micrograms per litre | 2 times a year | 2 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
p,p-DDE | micrograms per litre | 2 times a year | 2 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
p,p-DDT | micrograms per litre | 2 times a year | 2 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Polychlorinated biphenyls | micrograms per litre | 2 times a year | 2 | <0.10 | <0.10 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Selenium | micrograms per litre | 2 times a year | 2 | 0.3 | 0.3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Silver | micrograms per litre | 2 times a year | 2 | <1.0 | <1.0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | Every 12 days exactly | 30 | <1 | 46 | 35 | 15 | 50 | 28 | 0* | 60 | - | N/A | N/A | Yes
Zinc | micrograms per litre | 2 times a year | 2 | 30 | 47 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
* No 3DGM calculations required by licence this reporting period.
EPA Id. No. 3 | Site Description - Sludge pumping station
Site Code 5CB0600
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 July 2019 to 30 June 2020
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Number of measurements | Limit | Actual | Limit | Actual | Limits
Aldrin | micrograms per litre | Monthly | 12 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
alpha-BHC | micrograms per litre | Monthly | 12 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Arsenic | micrograms per litre | Weekly | 52 | 2.2 | 34.9 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
beta-BHC | micrograms per litre | Monthly | 12 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Cadmium | micrograms per litre | Weekly | 52 | 0.3 | 5.3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Chlordane, total | micrograms per litre | Monthly | 12 | <0.020 | <0.020 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Chromium | micrograms per litre | Weekly | 52 | 4 | 63.2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Copper | micrograms per litre | Weekly | 52 | 102 | 2000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Dieldrin | micrograms per litre | Monthly | 12 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Endosulfan | micrograms per litre | Monthly | 12 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Endrin | micrograms per litre | Monthly | 12 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
gamma-BHC (Lindane) | micrograms per litre | Monthly | 12 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Heptachlor | micrograms per litre | Monthly | 12 | <0.005 | <0.005 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Heptachlor epoxide | micrograms per litre | Monthly | 12 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Hexachlorobenzene | micrograms per litre | Monthly | 12 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Lead | micrograms per litre | Weekly | 52 | 11.5 | 254 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Mercury | micrograms per litre | Weekly | 52 | <0.1 | 0.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Methoxychlor | micrograms per litre | Monthly | 12 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nickel | micrograms per litre | Weekly | 52 | 4 | 90 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | Every 6 days exactly | 61 | 12.9 | 55.5 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Oil and Grease | milligrams per litre | Every 6 days exactly | 61 | 3 | 265 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
p,p-DDD | micrograms per litre | Monthly | 12 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
p,p-DDE | micrograms per litre | Monthly | 12 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
p,p-DDT | micrograms per litre | Monthly | 12 | <0.010 | <0.010 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Polychlorinated biphenyls | micrograms per litre | Monthly | 12 | <0.10 | <0.10 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Selenium | micrograms per litre | Weekly | 52 | 0.5 | 20.9 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Silver | micrograms per litre | Weekly | 52 | <1.0 | 16 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Solids | percent by weight | Every 6 days exactly | 61 | <0.10 | 1.44 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Zinc | micrograms per litre | Weekly | 52 | 304 | 5140 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 10 | Site Description - Pump well between clarifier and the sludge line
Site Code 5SG0601
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 July 2019 to 30 June 2020
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Number of measurements | Limit | Actual | Limit | Actual | Limits
Total Solids | percent by weight | Every 6 days exactly | 61 | <0.10 | 15.6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 11 | Site Description - Scum Pump Well
Site Code 5CC0600
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 July 2019 to 30 June 2020
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Number of measurements | Limit | Actual | Limit | Actual | Limits
Total Solids | percent by weight | Every 6 days exactly | 61 | <0.10 | 6.31 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
VOLUME MONITORING
Annual Summary
1 July 2019 to 30 June 2020
|  |  | Unit of | Sampling | No. of times measured during the year |  |  | Volume | Within
Monitoring Point |  |  | Measurement | Frequency |  |  | Maximum | Limit | Limits?
Point 1 - Ocean Outfall |  |  | kilolitres per day | Daily | 366 |  | 274094 | 510000 | Yes
Point 3 - Sludge Pumping Station |  |  | kilolitres per day | Daily | 366 |  | 2521 | 5000 | Yes
Point 10 - Sludge Dilution |  |  | kilolitres per day | Daily | 366 |  | 0 | N/A | N/A
Point 11 - Scum Pumping Station |  |  | kilolitres per day | Daily | 366 |  | 91 | N/A | N/A
Point 12 - Total Volume |  |  | kilolitres per day | Daily | 366 |  | 275700 | N/A | N/A
Point 13 - Treated Volume |  |  | kilolitres per day | Daily | 366 |  | 125270 | N/A | N/A
Point 17 - Bypass Volume |  |  | kilolitres per day | Daily | 366 |  | 150840 | N/A | N/A