## Cessnock
CESSNOCK WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - JULY 2021
|  | Environment Protection Licence No. 227 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 2 August 2021 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 19 August 2021 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 2 |  | Site Description - Reclaimed Water Storage Tank
Site Code 5TE8459
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 July 2021 to 31 July 2021
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 5 | 12 | 10.5 | 22 | N/A | N/A | 45 | 22 | Yes
Chlorophyll a | Chlorophyll a | micrograms per litre | (ug/L) | Weekly | WEEKLY | 4 | <1 | 43.25 | 26.5 | 119 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 8.61 | 10.8075 | 10.96 | 12.7 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 19.38 | 19.38 | 19.38 | 19.38 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Fortnightly | FORTNIGHTLY | 2 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 0.18 | 0.215 | 0.2 | 0.28 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids* | TSS(a) | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <1 | 5.65 | 6.47 | 8.66 | N/A | N/A | 70 | 8.66 | Yes
pH^ | pH | pH | pH | Weekly | WEEKLY | 4 | 6.89 | 6.9625 | 6.965 | 7.03 | N/A | N/A | 6.5 - 8.5 | 6.89 - 7.03 | Yes
* For the purpose of determining compliance with TSS limit, the concentration of TSS in samples collected shall be determined by; TSS(a)(mg/L) = TSS(b)(mg/L) minus 0.1 times chlorophyll 'a' (ug/L)
^ Condition L3.6 states that for the purposes of determining compliance with the licence limit for pH, the Licensee will be deemed to have complied with the pH licence limit provided the pH of the secondary effluent from the secondary clarifiers entering the tertiary ponds is within the range 6.5-8.5 for more than 90 percent of the samples collected.
EPA Id. No. 1 |  | Site Description - Outlet of No.3 Maturation Pond
Site Code 5OV0700
[6 empty] | No. of times measured during the month for licence reporting** | Monthly Summary
1 July 2021 to 31 July 2021
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Chlorophyll 'a' | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Chlorophyll a | Chlorophyll a | micrograms per litre | (ug/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS(b) | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
** No samples were collected as no discharge occurred during the month
Note: For pollutants with less than four samples measured during the monthly period see below for interpretation of summary tables: One required sample for licence reporting: Min, Mean, Median and Max values are all the exact data point Two required samples for licence reporting: Min and Max values are the two exact data points Three required samples for licence reporting: Min, Median and Max values are the three exact data points
VOLUME MONITORING |  |  | 51
Monthly Summary
1 July 2021 to 31 July 2021
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
|  |  |  | Measurement |  | Frequency | [5 empty] | Limit
Point 1 - Overflow from Pond 3 Weir |  |  | 4 | kilolitres per day | 2 | Daily | 31 |  | 0 | 0 | 0 | N/A | N/A
Point 2 - Discharge from Reclaimed Water Storage Tank at TTP |  |  | 3 | kilolitres per day | 10346 | Daily | 31 |  | 4014 | 5738.2258 | 7602 | 35000 | Yes
Chlorophyll 'a'
Chlorophyll 'a'
Note on D50: awebb: Last row of flow table