## Cessnock
CESSNOCK WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - APRIL 2025
|  | Environment Protection Licence No. 227 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 7 May 2025 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 21 May 2025 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 2 |  | Site Description - Reclaimed Water Storage Tank
Site Code 5TE8459
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 April 2025 to 30 April 2025
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Chlorophyll a | Chlorophyll a | micrograms per litre | (ug/L) | Weekly | WEEKLY | 5 | 2 | 3.04 | 2.6 | 4.2 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL | (cfu/100mL) | Weekly | WEEKLY | 5 | <10 | 287 | ~32 | ~1200 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | 0.08 | 0.712 | 0.1 | 2.02 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | 0.69 | 2.108 | 1.13 | 4.48 | N/A | N/A | 20 | 4.48 | Yes
Oil and Grease | Grease | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | <2 | 2 | <2 | 3 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | <0.05 | 0.072 | 0.05 | 0.14 | N/A | N/A | 5 | 0.14 | Yes
Total Suspended Solids | TSS(a) | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | 2.74 | 4.976 | 3.76 | 7.8 | N/A | N/A | N/A | N/A | Yes
pH | pH | pH | pH | Weekly | WEEKLY | 5 | 7.08 | 7.248 | 7.28 | 7.37 | N/A | N/A | 6.5 - 8.5 | 7.08 - 7.37 | Yes
EPA Id. No. 3 |  | Site Description - Secondary Treated Effluent
Site Code 5SI0750
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 April 2025 to 30 April 2025
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | <2 | 4.2 | 3 | 9 | N/A | N/A | 20 | 9 | Yes
Faecal Coliforms | FC | colony forming units per 100 mL | (cfu/100mL) | Weekly | WEEKLY | 5 | 11000 | 82600 | 55000 | ~170000 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | 0.3 | 0.432 | 0.43 | 0.58 | N/A | N/A | 5 | 0.58 | Yes
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | 4.41 | 6.122 | 5.4 | 9.9 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | <2 | <2 | <2 | 2 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | 0.51 | 0.982 | 0.72 | 1.76 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS(a) | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | 2 | 9.6 | 4 | 33 | N/A | N/A | 25 | 33 | No
pH | pH | pH | pH | Weekly | WEEKLY | 5 | 7.26 | 7.404 | 7.42 | 7.49 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 1 |  | Site Description - Outlet of No.3 Maturation Pond
Site Code 5OV0700
[6 empty] | No. of times measured during the month for licence reporting** | Monthly Summary
1 April 2025 to 30 April 2025
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Chlorophyll 'a' | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Special Frequency 1 |  | 1 | 5 | 5 | 5 | 5 | N/A | N/A | N/A | N/A | N/A
Chlorophyll a | Chlorophyll a | micrograms per litre | (ug/L) | Special Frequency 1 |  | 1 | 45.6 | 45.6 | 45.6 | 45.6 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Special Frequency 1 |  | 1 | 1.74 | 1.74 | 1.74 | 1.74 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Special Frequency 1 |  | 1 | 4.54 | 4.54 | 4.54 | 4.54 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Special Frequency 1 |  | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Special Frequency 1 |  | 1 | 1.35 | 1.35 | 1.35 | 1.35 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS(b) | milligrams per litre | (mg/L) | Special Frequency 1 |  | 1 | 15 | 15 | 15 | 15 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Special Frequency 1 |  | 1 | 7.61 | 7.61 | 7.61 | 7.61 | N/A | N/A | N/A | N/A | N/A
Note: For pollutants with less than four samples measured during the monthly period see below for interpretation of summary tables: One required sample for licence reporting: Min, Mean, Median and Max values are all the exact data point Two required samples for licence reporting: Min and Max values are the two exact data points Three required samples for licence reporting: Min, Median and Max values are the three exact data points
VOLUME MONITORING |  |  | 57
Monthly Summary
1 April 2025 to 30 April 2025
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
|  |  |  | Measurement |  | Frequency | [5 empty] | Limit
Point 1 - Overflow from Pond 3 Weir |  |  | 4 | kilolitres per day | 2 | Daily | 30 |  | 0 | 935 | 8688 | N/A | N/A
Point 2 - Discharge from Reclaimed Water Storage Tank at TTP |  |  | 3 | kilolitres per day | 10346 | Daily | 30 |  | 6022 | 7262 | 9473 | 35000 | Yes
** No samples were collected as no discharge occurred during the month
Chlorophyll 'a'
Chlorophyll 'a'
15500
N/A
N/A
Note on D66: awebb: Last row of flow table