## Cessnock
CESSNOCK WASTEWATER TREATMENT WORKS - ANNUAL POLLUTION MONITORING SUMMARY - 2020
| Environment Protection Licence No. 227 |  |  |  |  | Licensee | Hunter Water Corporation
| Date Obtained: 4 January 2021 | [5 empty] | 36 Honeysuckle Drive
| Date Published: 21 January 2021 | [5 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 2 | Site Description - Reclaimed Water Storage Tank
Site Code 5TE8459
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 January 2020 to 31 December 2020
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Weekly | 53 | <2 | 43 | 20 | 8 | 30 | 19 | N/A | N/A | 45 | 43 | Yes
Chlorophyll a | micrograms per litre | Weekly | 53 | <1.0 | 278 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | Weekly | 53 | 0.05 | 26.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | milligrams per litre | Monthly | 12 | 2 | 26.5 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Oil and Grease | milligrams per litre | Fortnightly | 26 | <2 | 6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH # | pH | Weekly | 53 | 6.8 | 8.26 | N/A | N/A | N/A | N/A | N/A | N/A | 6.5 - 8.5 | 6.80 - 8.26 | Yes
Phosphorus (total) | milligrams per litre | Weekly | 53 | 0.08 | 1.6 | N/A | N/A | 2 | 0.7 | N/A | N/A | N/A | N/A | Yes
Total Suspended Solids* | milligrams per litre | Weekly | 53 | <1 | 18 | 25 | 5 | 40 | 13 | N/A | N/A | 70 | 18 | Yes
* For the purpose of determining compliance with TSS limit, the concentration of TSS in samples collected shall be determined by; TSS(a)(mg/L) = TSS(b)(mg/L) minus 0.1 times chlorophyll 'a' (ug/L)
# Condition L3.6 states that for the purpose of determining compliance with the licence limit for pH, the licensee will be deemed to have complied with the pH licence limit provided that the pH of the secondary effluent from the humus clarifier entering the tertiary ponds is within the range 6.5 – 8.5 for more than 90 percent of the samples collected.
EPA Id. No. 1 | Site Description - The outlet of No. 3 maturation pond
Site Code 5OV0700
|  |  | No. of times measured during the year for licence reporting ** | Annual Summary
1 January 2020 to 31 December 2020
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Special Frequency 1 | 9 | 7 | 29 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Chlorophyll a | micrograms per litre | Special Frequency 1 | 9 | <1.0 | 723 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | Special Frequency 1 | 9 | 1.7 | 17.2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | milligrams per litre | Special Frequency 1 | 9 | 8.8 | 21.6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Oil and Grease | milligrams per litre | Special Frequency 1 | 9 | <2 | 6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH | pH | Special Frequency 1 | 9 | 7.48 | 9.91 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | milligrams per litre | Special Frequency 1 | 9 | 2.7 | 3.7 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | Special Frequency 1 | 9 | <1 | 37 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
** Six required sampled were missed during the Annual Return period
VOLUME MONITORING
Annual Summary
1 January 2020 to 31 December 2020
Monitoring Point |  |  | Unit of | Sampling | No. of times measured during the year |  |  |  |  | Volume | Within
|  |  | Measurement | Frequency |  |  | Minimum | Mean | Maximum | Limit | Limits?
Point 1 - Outlet of No.3 Maturation Pond |  |  | kilolitres per day | Daily | 366 |  | 0 | 61 | 5986 | N/A | N/A
Point 2 - Reclaimed Water Storage Tank at TTP |  |  | kilolitres per day | Daily | 366 |  | 2545 | 6546 | 15999 | 35000 | Yes