## Cessnock
CESSNOCK WASTEWATER TREATMENT WORKS - ANNUAL POLLUTION MONITORING SUMMARY - 2025
| Environment Protection Licence No. 227 |  |  |  |  | Licensee | Hunter Water Corporation
| Date Obtained 5 January 2026 | [5 empty] | 36 Honeysuckle Drive
| Date Published: 10 April 2026 | [5 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 | Site Description - The outlet of No. 3 maturation pond
Site Code 5OV0700
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 January 2025 to 31 December 2025
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Special Frequency 1 | 10 | <2 | 6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Chlorophyll a | micrograms per litre | Special Frequency 1 | 10 | <1 | 60.2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | colony forming units per 100 mL | Special Frequency 1 | 10 | ~80 | 170000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | Special Frequency 1 | 10 | 1.29 | 3.18 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | milligrams per litre | Special Frequency 1 | 10 | 2.3 | 7.7 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Oil and Grease | milligrams per litre | Special Frequency 1 | 10 | <2 | 2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH | pH | Special Frequency 1 | 10 | 7.14 | 7.7 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | milligrams per litre | Special Frequency 1 | 10 | 0.67 | 1.35 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | Special Frequency 1 | 10 | 3 | 21 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 2 | Site Description - Reclaimed Water Storage Tank
Site Code 5TE8459
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 January 2025 to 31 December 2025
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand** | milligrams per litre | Weekly | 52 | <2 | 8 | 20 | <2 | 30 | 2 | N/A | N/A | 45 | 4 | Yes
Chlorophyll a**** | micrograms per litre | Weekly | 11 | <1 | 17.1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms**** | colony forming units per 100 mL | Weekly | 41 | <2 | 74000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | Weekly | 52 | <0.05 | 3.16 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (total)* | milligrams per litre | Weekly | 44 | 0.6 | 8 | N/A | N/A | 15 | 4.5 | N/A | N/A | 20 | 8 | N/A
Oil and Grease | milligrams per litre | Weekly | 46 | <2 | 3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH | pH | Weekly | 52 | 6.97 | 7.73 | N/A | N/A | N/A | N/A | N/A | N/A | 6.5 - 8.5 | 6.97 - 7.73 | Yes
Phosphorus (total)*** | milligrams per litre | Weekly | 52 | <0.05 | 0.59 | N/A | N/A | 2 | 0.23 | N/A | N/A | 5 | 0.59 | Yes
Total Suspended Solids** | milligrams per litre | Weekly | 52 | <1 | 28 | 25 | 3 | 40 | 6 | N/A | N/A | 70 | 8 | Yes
* These results are calculated in accordance with the requirements of condition L3.4 from 24/03/2025 to 31/12/2025.
** These results are calculated in accordance with the requirements of condition L3.4 and L3.5 from 1/01/2025 to 24/03/2025 when the Environmental Protection Licence was changed.
*** 100 percentile results calculated in accordance with the requirements of condition L3.4 from 24/03/2025 to 31/12/2025.
**** Licence was varied on 24/03/2025 for EPL point 2. Requirement to test for Chlorophyll removed. Requirement to test for Faecal Coliforms included.
EPA Id. No. 3 | Site Description - Secondary treated effluent
Site Code 5SI0750
|  |  | No. of times measured during the year for licence reporting# | Annual Summary
1 January 2025 to 31 December 2025
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Weekly | 41 | <2 | 9 | N/A | N/A | 10 | 7 | N/A | N/A | 20 | 9 | Yes
Faecal Coliforms | colony forming units per 100 mL | Weekly | 41 | 2700 | 890000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | Weekly | 41 | 0.14 | 2.9 | N/A | N/A | 3 | 1.38 | N/A | N/A | 5 | 2.9 | Yes
Nitrogen (total) | milligrams per litre | Weekly | 41 | 3.8 | 10.6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Oil and Grease | milligrams per litre | Weekly | 41 | <2 | 3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH | pH | Weekly | 41 | 7.1 | 7.51 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | milligrams per litre | Weekly | 41 | 0.24 | 1.76 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | Weekly | 41 | <1 | 33 | N/A | N/A | 15 | 8 | N/A | N/A | 25 | 33 | No
# Licence was varied on 24/03/2025 to include EPL point 3.
VOLUME MONITORING
Annual Summary
1 January 2025 to 31 December 2025
Monitoring Point |  |  | Unit of | Sampling | No. of times measured during the year |  |  |  |  | Volume | Within
|  |  | Measurement | Frequency |  |  | Minimum | Mean | Maximum | Limit | Limits?
Point 1 - Outlet of No.3 Maturation Pond |  |  | kilolitres per day | Daily | 365 |  | 0 | 859 | 8688 | N/A | N/A
Point 2 - Reclaimed Water Storage Tank at TTP |  |  | kilolitres per day | Daily | 365 |  | 0 | 7219 | 9803 | 35000 | Yes