## Clarence Town
CLARENCE TOWN WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - JULY 2020
|  | Environment Protection Licence No. 13250 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 3 August 2020 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 20 August 2020 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 |  | Site Description - At the Effluent Pumping Station
Site Code 5CT0001
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 July 2020 to 31 July 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Aluminium | Al | milligrams per litre | (mg/L) | Yearly | YEARLY | 1 | 0.011 | 0.011 | 0.011 | 0.011 | N/A | N/A | N/A | N/A | N/A
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 22 | 25 | 24 | 30 | N/A | N/A | N/A | N/A | N/A
Cadmium | Cd (EPA) | milligrams per litre | (mg/L) | Yearly | YEARLY | 1 | <0.0002 | <0.0002 | <0.0002 | <0.0002 | N/A | N/A | N/A | N/A | N/A
Chloride | Cl- | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 56 | 56 | 56 | 56 | N/A | N/A | N/A | N/A | N/A
Chlorophyll a | Chlorophyll a (EPA) | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 41.7 | 59.3 | 57.1 | 81.1 | N/A | N/A | N/A | N/A | N/A
Chromium | Cr (EPA) | milligrams per litre | (mg/L) | Yearly | YEARLY | 1 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | N/A | N/A | N/A | N/A | N/A
Conductivity | Cond | microsiemens per centimetre | (µS/cm) | Quarterly | QUARTERLY | 1 | 487 | 487 | 487 | 487 | N/A | N/A | N/A | N/A | N/A
Copper | Cu (EPA) | milligrams per litre | (mg/L) | Yearly | YEARLY | 1 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | (CFU/100 ml) | Monthly | MONTHLY | 1 | ~100 | ~100 | ~100 | ~100 | N/A | N/A | N/A | N/A | N/A
Iron | Fe (EPA) | milligrams per litre | (mg/L) | Yearly | YEARLY | 1 | 0.032 | 0.032 | 0.032 | 0.032 | N/A | N/A | N/A | N/A | N/A
Lead | Pb (EPA) | milligrams per litre | (mg/L) | Yearly | YEARLY | 1 | <0.0002 | <0.0002 | <0.0002 | <0.0002 | N/A | N/A | N/A | N/A | N/A
Magnesium | Mg | milligrams per litre | (mg/L) | Yearly | YEARLY | 1 | 4.4 | 4.4 | 4.4 | 4.4 | N/A | N/A | N/A | N/A | N/A
Manganese | Mn (EPA) | milligrams per litre | (mg/L) | Yearly | YEARLY | 1 | 0.0314 | 0.0314 | 0.0314 | 0.0314 | N/A | N/A | N/A | N/A | N/A
Mercury | Hg (EPA) | milligrams per litre | (mg/L) | Yearly | YEARLY | 1 | <0.0001 | <0.0001 | <0.0001 | <0.0001 | N/A | N/A | N/A | N/A | N/A
Nitrate | Nitrate | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 0.36 | 0.36 | 0.36 | 0.36 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 2.3 | 2.3 | 2.3 | 2.3 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly | WEEKLY | 4 | 7.58 | 7.635 | 7.62 | 7.72 | N/A | N/A | N/A | N/A | N/A
Potassium | TK | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 19.6 | 19.6 | 19.6 | 19.6 | N/A | N/A | N/A | N/A | N/A
Total Nitrogen | TN | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 5.2 | 5.2 | 5.2 | 5.2 | N/A | N/A | N/A | N/A | N/A
Total Phosphorous | TP | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 5.2 | 5.2 | 5.2 | 5.2 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 14 | 18.75 | 18.5 | 24 | N/A | N/A | N/A | N/A | N/A
Zinc | Zn (EPA) | milligrams per litre | (mg/L) | Yearly | YEARLY | 1 | 0.002 | 0.002 | 0.002 | 0.002 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 2 |  | Site Description - Overflow Spillway
Site Code 5OV3100
[6 empty] | No. of times measured during the month for licence reporting* | Monthly Summary
1 July 2020 to 31 July 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Chlorophyll a | Chlorophyll a | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrate | Nitrate | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | 10 | - | N/A
pH | pH | pH | pH | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Nitrogen | TN | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Phosphorous | TP | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
* No samples were collected as no overflow occurred during the month
EPA Id. No. 5 |  | Site Description - Pumped Discharge to Wallaroo Creek
Site Code 5CT0035
[6 empty] | No. of times measured during the month for licence reporting** | Monthly Summary
1 July 2020 to 31 July 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Chlorophyll a | Chlorophyll a | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrate | Nitrate | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | 10 | - | N/A
pH | pH | pH | pH | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Nitrogen | TN | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Phosphorous | TP | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
** No samples were collected as no discharge occurred during the month
Note: For pollutants with less than four samples measured during the monthly period see below for interpretation of summary tables: One required sample for licence reporting: Min, Mean, Median and Max values are all the exact data point Two required samples for licence reporting: Min and Max values are the two exact data points Three required samples for licence reporting: Min, Median and Max values are the three exact data points
VOLUME MONITORING |  |  | 84
Monthly Summary
1 July 2020 to 31 July 2020
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
|  |  |  | Measurement |  | Frequency | [5 empty] | Limit
Point 1 - At the Effluent Pumping Station |  |  | 4 | kilolitres per day |  | Daily | 31 |  | 0 | 230 | 623 | 2800 | Yes
Point 2 - Overflow Spillway |  |  | 9 | kilolitres per day |  | Daily when discharging | 0 |  | 0 | 0 | 0 | N/A | N/A
Point 5 - Pumped Discharge to Wallaroo Creek |  |  | 5 | kilolitres per day |  | Daily | 31 |  | 0 | 0 | 0 | N/A | N/A
Point 6 - Creek Flow Monitoring |  |  | 11 | kilolitres per day |  | Daily when discharging | 0 |  | 0 | 0 | 0 | N/A | N/A
Chlorophyll 'a'
Note on D77: awebb: Last row of flow table