## Dungog WTP
| DUNGOG WATER TREATMENT PLANT - MONTHLY POLLUTION MONITORING SUMMARY - NOVEMBER 2022 | [11 empty] | 2022-11-01
| Environment Protection Licence No. 2863 |  |  |  |  | Licensee | Hunter Water Corporation
| Date Obtained: 2 December 2022 | [5 empty] | 36 Honeysuckle Drive
| Date Published: | [5 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 | Site Description - Sludge Lagoon 1 Outlet Pit
Site Code 1610116
|  |  | No. of times measured during the month for licence reporting | Monthly Summary
01 November 2022 to 30 November 2022
| Unit of | Sampling |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Aluminium (Soluble) | milligrams per litre | Monthly | 1 | 0.022 | 0.022 | 0.022 | 0.022 | N/A | N/A | TBD | N/A | N/A
Total Chlorine | milligrams per litre | Monthly | 1 | <0.1 | <0.1 | <0.1 | <0.1 | N/A | N/A | TBD | N/A | N/A
Fluoride | milligrams per litre | Monthly | 1 | <0.1 | <0.1 | <0.1 | <0.1 | N/A | N/A | TBD | N/A | N/A
Iron | milligrams per litre | Monthly | 1 | 0.678 | 0.678 | 0.678 | 0.678 | N/A | N/A | N/A | N/A | N/A
Manganese | milligrams per litre | Monthly | 1 | 1.04 | 1.04 | 1.04 | 1.04 | N/A | N/A | N/A | N/A | N/A
pH | pH | Monthly | 1 | 6.2 | 6.2 | 6.2 | 6.2 | N/A | N/A | TBD | N/A | N/A
Total Suspended Solids | milligrams per litre | Monthly | 1 | 2 | 2 | 2 | 2 | N/A | N/A | TBD | N/A | N/A
Aluminium (Soluble) is the result after filtration through 0.45 micron filter.
EPA Id. No. 2 | Site Description - Sludge Lagoon 2 Outlet Pit
Site Code 1610117
|  |  | No. of times measured during the month for licence reporting | Monthly Summary
01 November 2022 to 30 November 2022
| Unit of | Sampling |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Aluminium (Soluble) | milligrams per litre | Monthly | - | - | - | - | - | N/A | N/A | TBD | N/A | N/A
Total Chlorine | milligrams per litre | Monthly | - | - | - | - | - | N/A | N/A | TBD | N/A | N/A
Fluoride | milligrams per litre | Monthly | - | - | - | - | - | N/A | N/A | TBD | N/A | N/A
Iron | milligrams per litre | Monthly | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Manganese | milligrams per litre | Monthly | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | Monthly | - | - | - | - | - | N/A | N/A | TBD | N/A | N/A
Total Suspended Solids | milligrams per litre | Monthly | - | - | - | - | - | N/A | N/A | TBD | N/A | N/A
Aluminium (Soluble) is the result after filtration through 0.45 micron filter.
EPA Id. No. 3 | Site Description - Stormwater culvert at boundary of plant on the north side of Wade Street
Site Code 1610111
|  |  | No. of times measured during the month for licence reporting | Monthly Summary
01 November 2022 to 30 November 2022
| Unit of | Sampling |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Aluminium (Soluble) | milligrams per litre | Monthly | 1 | <0.005 | <0.005 | <0.005 | <0.005 | N/A | N/A | TBD | N/A | N/A
Total Chlorine | milligrams per litre | Monthly | 1 | <0.1 | <0.1 | <0.1 | <0.1 | N/A | N/A | TBD | N/A | N/A
Fluoride | milligrams per litre | Monthly | 1 | 0.1 | 0.1 | 0.1 | 0.1 | N/A | N/A | 1.5 | 0.1 | Yes
Iron | milligrams per litre | Monthly | 1 | 0.267 | 0.267 | 0.267 | 0.267 | N/A | N/A | N/A | N/A | N/A
Manganese | milligrams per litre | Monthly | 1 | 0.462 | 0.462 | 0.462 | 0.462 | N/A | N/A | N/A | N/A | N/A
pH | pH | Monthly | 1 | 6.8 | 6.8 | 6.8 | 6.8 | N/A | N/A | 6.5 - 8.5 | 6.8 | Yes
Total Suspended Solids | milligrams per litre | Monthly | 1 | 1 | 1 | 1 | 1 | N/A | N/A | 50 | 1 | Yes
Aluminium (Soluble) is the result after filtration through 0.45 micron filter.
"Note: For pollutants with less than four samples measured during the monthly period see below for interpretation of summary tables: One required sample for licence reporting: Min, Mean, Median and Max values are all the exact data point Two required samples for licence reporting: Min and Max values are the two exact data points Three required samples for licence reporting: Min, Median and Max values are the three exact data points"
VOLUME MONITORING
Flow Monitoring
|  |  |  | No. of times measured during the month | Monthly Summary
01 November 2022 to 30 November 2022
|  | Unit of | Sampling |  |  |  |  | Volume | Within
Monitoring Point |  | Measurement | Frequency |  | Minimum | Mean | Maximum | Limit** | Limits
Point 3 - Stormwater Culvert at Boundary of plant |  | kilolitres per day | Daily | 30 | 180 | 302 | 760 | 2000** | Yes
** Volume limit may be exceeded if the discharge is due to planned maintenance and the EPA is notified and approves the additional discharge prior to the activity, or if caused by emergency activity and the EPA is notified as soon as is possible