## Dungog WTP
DUNGOG WATER TREATMENT PLANT - ANNUAL POLLUTION MONITORING SUMMARY - 2019-2020
| Environment Protection Licence No. 2863 |  |  |  |  | Licensee | Hunter Water Corporation
| Date Obtained: 30 March 2020 | [5 empty] | 36 Honeysuckle Drive
| Date Published: 21 April 2020 | [5 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 | Site Description - Sludge Lagoon 1 Outlet Pit
Site Code 1610116
|  |  | No. of times measured during the year for licence reporting | Annual Summary
30 March 2019 to 29 March 2020
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Aluminium (Soluble) | milligrams per litre | Monthly | 8* | <0.005 | 0.021 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Total Chlorine | milligrams per litre | Monthly | 8* | <0.10 | 0.13 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Fluoride | milligrams per litre | Monthly | 8* | <0.10 | 0.12 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Iron | milligrams per litre | Monthly | 8* | 0.035 | 11.6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Manganese | milligrams per litre | Monthly | 8* | 0.068 | 7.36 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH | pH | Monthly | 8* | 6.4 | 7.5 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Total Suspended Solids | milligrams per litre | Monthly | 8* | <1 | 12 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Aluminium (Soluble) is the result after filtration through 0.45 micron filter.
*Only 8 samples were collected as Sludge Lagoon 1 was offline between 20/12/19 and 29/03/20.
EPA Id. No. 2 | Site Description - Sludge Lagoon 2 Outlet Pit
Site Code 1610117
|  |  | No. of times measured during the year for licence reporting # | Annual Summary
30 March 2019 to 29 March 2020
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Aluminium (Soluble) | milligrams per litre | Monthly | 4** | 0.012 | 0.072 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Total Chlorine | milligrams per litre | Monthly | 4** | <0.10 | 0.1 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Fluoride | milligrams per litre | Monthly | 4** | <0.10 | 0.11 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Iron | milligrams per litre | Monthly | 4** | 0.042 | 1.06 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Manganese | milligrams per litre | Monthly | 4** | 1.26 | 2.31 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH | pH | Monthly | 4** | 6 | 6.7 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Total Suspended Solids | milligrams per litre | Monthly | 4** | <1 | 3 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Aluminium (Soluble) is the result after filtration through 0.45 micron filter.
**Only 4 samples were collected as Sludge Lagoon 2 was offline between 30/03/19 and 18/12/19.
EPA Id. No. 3 | Site Description - Stormwater culvert at boundary of plant on the north side of Wade Street
Site Code 1610111
|  |  | No. of times measured during the year for licence reporting | Annual Summary
30 March 2019 to 29 March 2020
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Aluminium (Soluble) | milligrams per litre | Monthly | 12 | <0.005 | 0.056 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Total Chlorine | milligrams per litre | Monthly | 12 | <0.10 | 0.15 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Fluoride | milligrams per litre | Monthly | 12 | <0.10 | 0.27 | N/A | N/A | N/A | N/A | N/A | N/A | 1.5 | 0.27 | Yes
Iron | milligrams per litre | Monthly | 12 | 0.456 | 3.07 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Manganese | milligrams per litre | Monthly | 12 | 0.62 | 3.69 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH | pH | Monthly | 12 | 6.8 | 7.5 | N/A | N/A | N/A | N/A | N/A | N/A | 6.5 - 8.5 | 6.8 - 7.5 | Yes
Total Suspended Solids | milligrams per litre | Monthly | 12 | <1 | 9 | N/A | N/A | N/A | N/A | N/A | N/A | 50 | 9 | Yes
Aluminium (Soluble) is the result after filtration through 0.45 micron filter.
VOLUME MONITORING
Flow Monitoring
|  |  |  | No. of times measured during the year | Annual Summary
30 March 2019 to 29 March 2020
|  | Unit of | Sampling |  |  | Volume | Within
Monitoring Point |  | Measurement | Frequency |  | Maximum | Limit*** | Limits?
Point 3 - Stormwater Culvert at Boundary of plant |  | kilolitres per day | Daily | 366 | 3660 | 2000 | See Note ***
***Volume limit may be exceeded if the discharge is due to planned maintenance and the EPA is notified and approves the additional discharge prior to the activity, or if caused by emergency activity and the EPA is notified as soon as is possible
The Volume limit was exceeded on 5 September 2019 as part of an emergency response which undertaken to ensure that safe drinking water was supplied from Dungog Water Treatment Plant. The EPA were notified of the details of emergency response and
exceedance of the volume limit as soon as practical. Volume limit was complied with at all other times.