## Dungog WTP
DUNGOG WATER TREATMENT PLANT - ANNUAL POLLUTION MONITORING SUMMARY - 2021-2022
| Environment Protection Licence No. 2863 |  |  |  |  | Licensee | Hunter Water Corporation
| Date Obtained: 1 April 2022 | [5 empty] | 36 Honeysuckle Drive
| Date Published: 22 April 2022 | [5 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 | Site Description - Sludge Lagoon 1 Outlet Pit
|  |  | No. of times measured during the year for licence reporting | Annual Summary
30 March 2021 to 29 March 2022
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Aluminium (Soluble) | milligrams per litre | Monthly | 6* | 0.07 | 0.027 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Total Chlorine | milligrams per litre | Monthly | 6* | <0.1 | <0.1 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Fluoride | milligrams per litre | Monthly | 6* | <0.1 | 0.2 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Iron | milligrams per litre | Monthly | 6* | 13.6 | 78.6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Manganese | milligrams per litre | Monthly | 6* | 3.81 | 17.1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH | milligrams per litre | Monthly | 6* | 6.4 | 7 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Total Suspended Solids | milligrams per litre | Monthly | 6* | <1 | 58 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Aluminium (Soluble) is the result after filtration through 0.45 micron filter.
* Samples from EPL Points 1 and 2 are only collected when discharge from the individual lagoon is occurring. During lagoon changeover in late September both lagoons were discharging, resulting in a sample being taken and reported from both lagoons for September.
EPA Id. No. 2 | Site Description - Sludge Lagoon 2 Outlet Pit
|  |  | No. of times measured during the year for licence reporting # | Annual Summary
30 March 2021 to 29 March 2022
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Aluminium (Soluble) | milligrams per litre | Monthly | 7** | 0.006 | 0.054 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Total Chlorine | milligrams per litre | Monthly | 7** | <0.1 | <0.1 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Fluoride | milligrams per litre | Monthly | 7** | <0.1 | 0.1 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Iron | milligrams per litre | Monthly | 7** | 0.006 | 4.78 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Manganese | milligrams per litre | Monthly | 7** | 0.287 | 2.05 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH | milligrams per litre | Monthly | 7** | 5.9 | 7 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Total Suspended Solids | milligrams per litre | Monthly | 7** | <1 | 8 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Aluminium (Soluble) is the result after filtration through 0.45 micron filter.
** Samples from EPL Points 1 and 2 are only collected when discharge from the individual lagoon is occurring. During lagoon changeover in late September both lagoons were discharging, resulting in a sample being taken and reported from both lagoons for September.
EPA Id. No. 3 | Site Description - Stormwater culvert at boundary of plant on the north side of Wade Street
|  |  | No. of times measured during the year for licence reporting | Annual Summary
30 March 2021 to 29 March 2022
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Aluminium (Soluble) | milligrams per litre | Monthly | 12 | <0.005 | 0.029 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Total Chlorine | milligrams per litre | Monthly | 12 | <0.1 | <0.1 | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A
Fluoride | milligrams per litre | Monthly | 12 | 0.1 | 0.4 | N/A | N/A | N/A | N/A | N/A | N/A | 1.5 | 0.4 | Yes
Iron | milligrams per litre | Monthly | 12 | 0.411 | 7.48 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Manganese | milligrams per litre | Monthly | 12 | 0.431 | 2.01 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH | milligrams per litre | Monthly | 12 | 6.6 | 7.8 | N/A | N/A | N/A | N/A | N/A | N/A | 6.5 - 8.5 | 6.6 - 7.8 | Yes
Total Suspended Solids | milligrams per litre | Monthly | 12 | <1 | 88 *** | N/A | N/A | N/A | N/A | N/A | N/A | 50 | 88 *** | No ***
Aluminium (Soluble) is the result after filtration through 0.45 micron filter.
*** Note - the total suspended solids result for the sample collected on 29 March 2022 for EPL Point 3 (ie discharge from the site boundary) was 88 mg/L. The sample was collected during a period of intense rainfall in the Dungog area which resulted in increased stormwater flows discharging from site. The source of the elevated suspended solids is most likely sediment from stormwater runoff from the high intensity rain event. Additional sampling collected on the same day returned low suspended solids results further indicating that the discharge from the water treatment plant was not the source of elevated suspended solids recorded in the sample collected at EPL Point 3.
VOLUME MONITORING
Annual Summary
30 March 2021 to 29 March 2022
|  | Unit of | Sampling | No. of times measured during the year |  |  |  |  | Volume | Within
Monitoring Point |  | Measurement | Frequency |  |  | Minium | Mean | Maximum | Limit*** | Limits?
Point 3 - Stormwater Culvert at Boundary of plant |  | kilolitres per day | Daily | 365 |  | 50 | 322 | 2473**** | 2000 | No****
****Volume limit may be exceeded if the discharge is due to planned maintenance and the EPA is notified and approves the additional discharge prior to the activity, or if caused by emergency activity and the EPA is notified as soon as is possible
The Volume limit was exceeded on 28 November 2021 as part of an emergency response which undertaken to ensure that safe drinking water was supplied from Dungog Water Treatment Plant. The EPA were notified of the details of emergency response and exceedance of the volume limit as soon as practical. Volume limit was complied with at all other times.