## Dungog
DUNGOG WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - APRIL 2020
|  | Environment Protection Licence No. 4197 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 5 May 2020 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 21 May 2020 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
Site Code 5DU0001 |  | Site Description - Effluent Storage Pond
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 April 2020 to 30 April 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency * |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 3 | 9 | 5 | 22 | N/A | N/A | N/A | N/A | N/A
Chlorophyll a | Chlorophyll a | micrograms per litre | (ug/L) | Weekly | WEEKLY | 4 | 2.9 | 56.2 | 25.95 | 170 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | (cfu/100ml) | Weekly | WEEKLY | 4 | <91 | 1663 | 1680 | 3200 | N/A | N/A | N/A | N/A | N/A
Nitrogen (Total) | TN | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 6.81 | 7.65 | 7.8 | 8.2 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly | WEEKLY | 4 | 7.45 | 7.9 | 7.72 | 8.71 | N/A | N/A | N/A | N/A | N/A
Total Phosphorus-unfiltered sample | TP | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 3.4 | 3.6 | 3.55 | 3.7 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 3 | 13.5 | 12.5 | 26 | N/A | N/A | N/A | N/A | N/A
Monitoring data for all samples collected from the Effluent Storage Pond during the month. Relevant samples from the complete data set have been attributed to discharge through each monitoring point and are presented below in separate tables. * As per the note under the licence condition M2.3, it is acceptable for the licensee to take a single sample of Storage Pond water (5DU0001) monthly to meet the monitoring requirements for Points 3, 4 and 5, provided that sample is representative of waters discharged via Points 3, 4 and 5.
EPA Id. No. 3 |  | Site Description - Effluent Utilisation Pump
Site Code 5DU0001
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 April 2020 to 30 April 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency * |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly |  | 3 | 3 | 4 | 3 | 7 | N/A | N/A | N/A | N/A | N/A
Chlorophyll a | Chlorophyll a | micrograms per litre | (ug/L) | Weekly |  | 3 | 2.9 | 18.27 | 7.2 | 44.7 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | (cfu/100ml) | Weekly |  | 3 | <91 | 483.67 | 360 | ~1000 | N/A | N/A | N/A | N/A | N/A
Nitrogen (Total) | TN | milligrams per litre | (mg/L) | Weekly |  | 3 | 6.81 | 7.64 | 7.9 | 8.2 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Weekly |  | 3 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly |  | 3 | 7.45 | 7.63 | 7.56 | 7.88 | N/A | N/A | N/A | N/A | N/A
Total Phosphorus-unfiltered sample | TP | milligrams per litre | (mg/L) | Weekly |  | 3 | 3.4 | 3.6 | 3.7 | 3.7 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly |  | 3 | 3 | 9.33 | 3 | 22 | N/A | N/A | N/A | N/A | N/A
# No discharge occurred from Point 3 during the month.
Monitoring data is taken from the Effluent Storage Pond for each week that discharge occurred via Point 3. This monitoring data is from the same data set that comprises the Effluent Storage Pond provided under subsite code 5DU0001.
* As per the note under the licence condition M2.3, it is acceptable for the licensee to take a single sample of Storage Pond water monthly to meet the monitoring requirements for Points 3, 4 and 5, provided that sample is representative of waters discharged via Points 3, 4 and 5.
EPA Id. No. 4 |  | Site Description - Pump Discharges from Dam to Williams River
Site Code 5DU0001
[6 empty] | No. of times measured during the month for licence reporting # | Monthly Summary
1 April 2020 to 30 April 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency * |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Chlorophyll a | Chlorophyll a | micrograms per litre | (ug/L) | Weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | (cfu/100ml) | Weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (Total) | TN | milligrams per litre | (mg/L) | Weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Phosphorus-unfiltered sample | TP | milligrams per litre | (mg/L) | Weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
# No discharge occurred from Point 5 during the month.
Monitoring data is taken from the Effluent Storage Pond for each week that discharge occurred via Point 4. This monitoring data is from the same data set that comprises the Effluent Storage Pond provided under subsite code 5DU0001.
* As per the note under the licence condition M2.3, it is acceptable for the licensee to take a single sample of Storage Pond water monthly to meet the monitoring requirements for Points 3, 4 and 5, provided that sample is representative of waters discharged via Points 3, 4 and 5.
EPA Id. No. 5 |  | Site Description - Overflow Drain to Williams River
Site Code 5DU0016
[6 empty] | No. of times measured during the month for licence reporting ## | Monthly Summary
1 April 2020 to 30 April 2020
|  | Unit of |  | Sampling |  |  | 1 April 2020 to 30 April 2020 | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency * |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Chlorophyll a | Chlorophyll a | micrograms per litre | (ug/L) | Weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | (cfu/100ml) | Weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (Total) | TN | milligrams per litre | (mg/L) | Weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Phosphorus-unfiltered sample | TP | milligrams per litre | (mg/L) | Weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
## No discharge occurred from Point 5 during the month.
Monitoring data is taken from the Effluent Storage Pond for each week that discharge occurred via Point 5. This monitoring data is from the same data set that comprises the Effluent Storage Pond provided under subsite code 5DU0001.
* As per the note under the licence condition M2.3, it is acceptable for the licensee to take a single sample of Storage Pond water monthly to meet the monitoring requirements for Points 3, 4 and 5, provided that sample is representative of waters discharged via Points 3, 4 and 5.
EPA Id. No. 8 |  | Site Description - Humus Clarifier Effluent
Site Code 5DU0002
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 April 2020 to 30 April 2020
|  | Unit of |  | Sampling |  |  | 1 April 2020 to 30 April 2020 | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 34 | 36 | 36.5 | 38 | N/A | N/A | N/A | N/A | N/A
Chlorophyll a | Chlorophyll a | micrograms per litre | (ug/L) | Weekly | WEEKLY | 4 | 9.1 | 25.7 | 25.8 | 42.2 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | (cfu/100ml) | Weekly | WEEKLY | 4 | 2300000 | 2925000 | 2700000 | 4000000 | N/A | N/A | N/A | N/A | N/A
Nitrogen (Total) | TN | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 20.8 | 24.95 | 25.55 | 27.9 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <2 | 3 | 2.5 | 5 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly | WEEKLY | 4 | 7.12 | 7.1875 | 7.19 | 7.25 | N/A | N/A | N/A | N/A | N/A
Total Phosphorus-unfiltered sample | TP | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 4.4 | 5.175 | 5.25 | 5.8 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 45 | 50.25 | 50 | 56 | N/A | N/A | N/A | N/A | N/A
VOLUME MONITORING |  |  | 107
Monthly Summary
1 April 2020 to 30 April 2020
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  |  | Volume | Within Limits
|  |  |  | Measurement |  | Frequency |  |  | Maximum | Limit
Point 1 - Inflow to Plant |  |  | 3 | kilolitres per day | 1.12 | Daily | 30 |  | 1120 | N/A | N/A
Point 3 - Effluent Utilisation Pump |  |  | 4 | kilolitres per day | 2.9 | Daily during any discharge | 9 |  | 2900 | N/A | N/A
Point 4 - Pump Discharges from Dam to Williams River |  |  | 5 | kilolitres per day | 0 | Daily during any discharge | 0 |  | 0 | N/A | N/A
Point 5 - Overflow Drain to Williams River |  |  | 6 | kilolitres per day | 0 | Daily | 30 |  | 0 | N/A | N/A
Note on D99: awebb: Last row of flow table