## Farley
FARLEY WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - MARCH 2024
|  | Environment Protection Licence No. 733 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 3 April 2024 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 19 April 2024 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 |  | Site Description - Pond No. 2 overflow into Fishery Creek
Site Code 5SL2300
[6 empty] | No. of times measured during the month for licence reporting* | Monthly Summary
1 March 2024 to 31 March 2024
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Chlorophyll a | Chlorophyll a | micrograms per litre | (ug/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrate+Nitrite (Oxidised Nitrogen) | TON | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (Ammonia) | Ammonia | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (Total) | Total N | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Phosphorus (Total) | TP | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS(b) | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
*No samples were collected or analysed during the month as no overflow occurred during the month.
EPA Id. No. 4 |  | Site Description - Overflow weir from wet weather storage
Site Code 5OV2300
[6 empty] | No. of times measured during the month for licence reporting** | Monthly Summary
1 March 2024 to 31 March 2024
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Chlorophyll 'a' | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrate+Nitrite (Oxidised Nitrogen) | TON | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (Ammonia) | Ammonia | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Phosphorus (Total) | TP | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
**No samples were collected or analysed during the month as no overflow occurred during the month.
EPA Id. No. 7 |  | Site Description - Effluent quality downstream of membrane filtration system
Site Code 5DE2300
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 March 2024 to 31 March 2024
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Chlorophyll 'a' | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <2 | 2.25 | <2 | 3 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | Colony forming units per 100mL | CFU/100mL | Weekly | WEEKLY | 4 | <1 | 5.5 | 2 | 17 | N/A | N/A | N/A | N/A | N/A
Nitrate+Nitrite (Oxidised Nitrogen) | TON | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 1.36 | 1.36 | 1.36 | 1.36 | N/A | N/A | N/A | N/A | N/A
Nitrogen (Ammonia) | Ammonia | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <0.05 | 0.0725 | 0.065 | 0.11 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 2.16 | 2.16 | 2.16 | 2.16 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly | WEEKLY | 4 | 7.33 | 7.45 | 7.48 | 7.51 | N/A | N/A | N/A | N/A | N/A
Phosphorus (Total) | TP | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 0.34 | 0.43 | 0.35 | 0.68 | N/A | N/A | N/A | N/A | N/A
Total Kjeldal Nitrogen | TKN | milligrams per litre |  | Monthly | MONTHLY | 1 | 0.8 | 0.8 | 0.8 | 0.8 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 1 | 2.25 | 1.5 | 5 | N/A | N/A | N/A | N/A | N/A
Note: For pollutants with less than four samples measured during the monthly period see below for interpretation of summary tables: One required sample for licence reporting: Min, Mean, Median and Max values are all the exact data point Two required samples for licence reporting: Min and Max values are the two exact data points Three required samples for licence reporting: Min, Median and Max values are the three exact data points
VOLUME MONITORING |  |  | 76
Monthly Summary
1 March 2024 to 31 March 2024
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
|  |  |  | Measurement |  | Frequency | [5 empty] | Limit
Point 1 - Pond No. 2 overflow into Fishery Creek |  |  | 10 | kilolitres per day | 0 | Continuous | 31 |  | 0 | 0 | 0 | 35000 | Yes
Point 3 - Downstream of the membrane filtration system |  |  | 4 | kilolitres per day | 8656 | Continuous | 31 |  | 6670 | 8372.1613 | 15517 | 35000 | Yes
Point 4 - Overflow weir from wet weather storage |  |  | 6 | kilolitres per day | 0 | Continuous | 31 |  | 0 | 0 | 0 | 35000 | Yes
Point 5 - Flow to Reuse Customers |  |  | 7 | kilolitres per day | 0 | Continuous | 31 |  | 0 | 0 | 0 | N/A | N/A
Point 6 - Pond 2 Top Up |  |  | 8 | kilolitres per day | 0 | Continuous | 31 |  | 0 | 34.6452 | 358 | N/A | N/A
Combined Point 1, 3 and 4 |  |  | 13 | kilolitres per day | 8656 | Continuous | 31 |  | 6670 | 8372.1613 | 15517 | 35000 | Yes
As per EPL condition L4.3, the licensee may discharge up to 120,000 kL per day of effluent providing that the volume of flow in Fishery creek at the time of discharge at the discharge point exceeds the bank full capacity of Fishery Creek.
15500
N/A
N/A
Note on D65: awebb: Last row of flow table