## Karuah
KARUAH WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - FEBRUARY 2021
|  | Environment Protection Licence No. 10230 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 1 March 2021 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 18 March 2021 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 |  | Site Description - Effluent Irrigation Pump
Site Code 5SL3000
[6 empty] | No. of times measured during the month for licence reporting* | Monthly Summary
1 February 2021 to 28 February 2021
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Quarterly | QUARTERLY | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (Total) | Total N | milligrams per litre | (mg/L) | Quarterly | QUARTERLY | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Phosphorus (Total) | TP | milligrams per litre | (mg/L) | Quarterly | QUARTERLY | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Quarterly | QUARTERLY | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
*No samples were collected as no irrigation samples collected during the month
EPA Id. No. 2 |  | Site Description - Overflow Discharge pit
Site Code 5OV3000
[6 empty] | No. of times measured during the month for licence reporting ** | Monthly Summary
1 February 2021 to 28 February 2021
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | First 24 hrs. then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FCHdn | colony forming units per 100 mL | CFU/100mL | First 24 hrs. then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | First 24 hrs. then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
**No samples were collected as no discharge occurred during the month
EPA Id. No. 3 |  | Site Description - UV Disinfection plant
Site Code 5EE3000
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2021 to 28 February 2021
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 2 | 2 | 2 | 2 | N/A | N/A | 20 | 2 | Yes
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Monthly | MONTHLY | 1 | ~4 | ~4 | ~4 | ~4 | N/A | N/A | 500 | ~4 | Yes
NH3-N | Ammonia | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 0.87 | 0.87 | 0.87 | 0.87 | N/A | N/A | 5 | 0.87 | Yes
Nitrogen (Total) | Total N | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 4.8 | 4.8 | 4.8 | 4.8 | N/A | N/A | N/A | N/A | N/A
Phosphorus (Total) | TP | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 0.31 | 0.31 | 0.31 | 0.31 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | <1 | <1 | <1 | <1 | N/A | N/A | 30 | <1 | Yes
pH | pH | pH | pH | Monthly | MONTHLY | 1 | 7.07 | 7.07 | 7.07 | 7.07 | N/A | N/A | 6.5 - 8.5 | 7.07 | Yes
Note: For pollutants with less than four samples measured during the monthly period see below for interpretation of summary tables: One required sample for licence reporting: Min, Mean, Median and Max values are all the exact data point Two required samples for licence reporting: Min and Max values are the two exact data points Three required samples for licence reporting: Min, Median and Max values are the three exact data points
VOLUME MONITORING |  |  | 57
Monthly Summary
1 February 2021 to 28 February 2021
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
|  |  |  | Measurement |  | Frequency | [5 empty] | Limit
Point 1 - Effluent Irrigation |  |  | 3 | kilolitres per day | 1821 | Daily | 28 |  | 0 | 278 | 1935 | 3000 | Yes
Point 2 - Overflow Discharge |  |  | 5 | kilolitres per day | 0 | Daily | 28 |  | 0 | 0 | 0 | N/A | N/A
Chlorophyll 'a'
Chlorophyll 'a'
Note on D54: awebb: Last row of flow table