## Karuah
KARUAH WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - MARCH 2021
|  | Environment Protection Licence No. 10230 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 6 April 2021 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 23 April 2021 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 |  | Site Description - Effluent Irrigation Pump
Site Code 5SL3000
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 March 2021 to 31 March 2021
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Quarterly | QUARTERLY | 1 | 3 | 3 | 3 | 3 | N/A | N/A | N/A | N/A | N/A
Nitrogen (Total) | Total N | milligrams per litre | (mg/L) | Quarterly | QUARTERLY | 1 | 1.64 | 1.64 | 1.64 | 1.64 | N/A | N/A | N/A | N/A | N/A
Phosphorus (Total) | TP | milligrams per litre | (mg/L) | Quarterly | QUARTERLY | 1 | 0.27 | 0.27 | 0.27 | 0.27 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Quarterly | QUARTERLY | 1 | 3 | 3 | 3 | 3 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 2 |  | Site Description - Overflow Discharge pit
Site Code 5OV3000
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 March 2021 to 31 March 2021
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | First 24 hrs. then weekly |  | 3 | 5 | 6.6667 | 6 | 9 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FCHdn | colony forming units per 100 mL | CFU/100mL | First 24 hrs. then weekly |  | 3 | ~<9 | 1606.3333 | 910 | 3900 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | First 24 hrs. then weekly |  | 3 | 10 | 12.3333 | 11 | 16 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 3 |  | Site Description - UV Disinfection plant
Site Code 5EE3000
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 March 2021 to 31 March 2021
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | <2 | <2 | <2 | <2 | N/A | N/A | 20 | <2 | Yes
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Monthly | MONTHLY | 1 | ~2 | ~2 | ~2 | ~2 | N/A | N/A | 500 | ~2 | Yes
Nitrogen (Ammonia) | Ammonia | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 0.27 | 0.27 | 0.27 | 0.27 | N/A | N/A | 5 | 0.27 | Yes
Nitrogen (Total) | Total N | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 9.86 | 9.86 | 9.86 | 9.86 | N/A | N/A | N/A | N/A | N/A
Phosphorus (Total) | TP | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 0.86 | 0.86 | 0.86 | 0.86 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | <1 | <1 | <1 | <1 | N/A | N/A | 30 | <1 | Yes
pH | pH | pH | pH | Monthly | MONTHLY | 1 | 7.17 | 7.17 | 7.17 | 7.17 | N/A | N/A | 6.5 - 8.5 | 7.17 | Yes
Note: For pollutants with less than four samples measured during the monthly period see below for interpretation of summary tables: One required sample for licence reporting: Min, Mean, Median and Max values are all the exact data point Two required samples for licence reporting: Min and Max values are the two exact data points Three required samples for licence reporting: Min, Median and Max values are the three exact data points
VOLUME MONITORING |  |  | 57
Monthly Summary
1 March 2021 to 31 March 2021
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
|  |  |  | Measurement |  | Frequency | [5 empty] | Limit
Point 1 - Effluent Irrigation |  |  | 3 | kilolitres per day | 1821 | Daily | 31 |  | 0 | 446 | 2282 | 3000 | Yes
Point 2 - Overflow Discharge |  |  | 5 | kilolitres per day | 0 | Daily | 31 |  | 0 | 1699 | 12794 | N/A | N/A
Chlorophyll 'a'
Chlorophyll 'a'
Note on D54: awebb: Last row of flow table