## Karuah
KARUAH WASTEWATER TREATMENT WORKS - ANNUAL POLLUTION MONITORING SUMMARY - 2020-21
| Environment Protection Licence No. 10230 |  |  |  | Hunter Water Corporation
| Date Obtained: 5 October 2021 |  |  |  | 36 Honeysuckle Drive
| Date Published: 25 October 2021 |  |  |  | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 | Site Description - Flow meter on discharge line from effluent irrigation pump
Site Code 5SL3000
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 October 2020 - 30 September 2021
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Quarterly | 4 | <2 | 13 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (Total) | milligrams per litre | Quarterly | 4 | 1.35 | 6.85 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Phosphorus (Total) | milligrams per litre | Quarterly | 4 | 0.14 | 0.71 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | Quarterly | 4 | <1 | 5 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 2 | Site Description - Overflow discharge pit
Site Code 5OV3000
|  |  | No. of times measured during the year for licence reporting* | Annual Summary
1 October 2020 - 30 September 2021
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | First 24 hrs then weekly | 29 | <2 | 55 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | colony forming units per 100 mL | First 24 hrs then weekly | 29 | ~<1 | 3900 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | First 24 hrs then weekly | 29 | <1 | 56 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
*No samples were collected as no overflow occurred during the reporting period
EPA Id. No. 3 | Site Description - Discharge from the UV disinfection plant to the effluent storage dam
Site Code 5EE3000
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 October 2020 - 30 September 2021
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Monthly | 12 | <2 | 8 | N/A | N/A | 15 | 5 | N/A | N/A | 20 | 8 | Yes
Faecal Coliforms | colony forming units per 100 mL | Monthly | 12 | <2 | 320 | N/A | N/A | 200 | 5 | N/A | N/A | 500 | 320 | Yes
Nitrogen (ammonia) | milligrams per litre | Monthly | 12 | 0.18 | 1.1 | N/A | N/A | 3 | 1.1 | N/A | N/A | 5 | 1.1 | Yes
Nitrogen (Total) | milligrams per litre | Monthly | 12 | 2.3 | 15.9 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Phosphorus (Total) | milligrams per litre | Monthly | 12 | 0.29 | 1.9 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | Monthly | 12 | <1 | 18 | N/A | N/A | 20 | 9 | N/A | N/A | 30 | 18 | Yes
pH | pH | Monthly | 12 | 6.96 | 7.53 | N/A | N/A | N/A | N/A | N/A | N/A | 6.5 - 8.5 | 6.96 - 7.53 | Yes
VOLUME MONITORING
Annual Summary
1 October 2020 - 30 September 2021
Monitoring Point |  | Unit of | Sampling | No. of times measured during the year |  |  |  |  | Volume | Within
|  | Measurement | Frequency |  |  | Minimum | Mean | Maximum | Limit | Limits?
Point 1 - Effluent Irrigation |  | kilolitres per day | Daily | 365 |  | 0 | 237.6685 | 2342 | 3000 | Yes
Point 2 - Overflow Discharge |  | kilolitres per day | Daily | 365 |  | 0 | 358 | 7266 | N/A | N/A