## Kearsley
KEARSLEY WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - JANUARY 2021
|  | Environment Protection Licence No. 3232 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 1 February 2021 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 19 February 2021 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 |  | Site Description - Discharge from No.2 Oxidation Pond
Site Code 5SL2600
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 January 2021 to 31 January 2021
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 9 | 318 | 51.5 | 1160 | N/A | N/A | 60 | 1160 | Yes*
Chlorophyll a | Chlorophyll a | micrograms per litre | (ug/L) | Weekly | WEEKLY | 4 | 262 | 553 | 539.5 | 871 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 0.08 | 0.08 | 0.08 | 0.08 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 17.3 | 17.3 | 17.3 | 17.3 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly | WEEKLY | 4 | 7.02 | 8.7125 | 8.885 | 10.06 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 4.3 | 4.3 | 4.3 | 4.3 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 126 | 399.5 | 171 | 1130 | N/A | N/A | 70 | 1130 | Yes*
*The licensee is not taken to have exceeded a quality limit specified in this licence for pH, BOD or TSS if the licensee shows that the level of chlorophyll-a in the oxidation ponds during any exceedance was 100 ug/L or more (showing that the exceedance was caused by excessive algal growth).
Note: For pollutants with less than four samples measured during the monthly period see below for interpretation of summary tables: One required sample for licence reporting: Min, Mean, Median and Max values are all the exact data point Two required samples for licence reporting: Min and Max values are the two exact data points Three required samples for licence reporting: Min, Median and Max values are the three exact data points
VOLUME MONITORING |  |  | 31
Monthly Summary
1 January 2021 to 31 January 2021
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
|  |  |  | Measurement |  | Frequency | [5 empty] | Limit
Point 1 - Discharge from No.2 Oxidation Pond |  |  | 7 | kilolitres per day | 0.80514 | Daily | 31 |  | 177 | 257 | 483 | 2500 | Yes
Chlorophyll 'a'
Chlorophyll 'a'
Note on D31: awebb: Last row of flow table