## Kearsley
KEARSLEY WASTEWATER TREATMENT WORKS - ANNUAL POLLUTION MONITORING SUMMARY - 2020-21
| Environment Protection Licence No. 3232 | [7 empty] | Licensee | Hunter Water Corporation
| Date Obtained: 6 April 2021 | [8 empty] | 36 Honeysuckle Drive
| Date Published: 23 April 2021 | [8 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 | Site Description - Discharge from the No.2 Oxidation Pond
Site Code 5SL2600
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 April 2020 to 31 March 2021
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
pH | pH | Weekly | 53 | 7.02 | 10.13 | N/A | N/A | 6.5 - 8.5 | 7.57 - 9.61 | N/A | N/A | N/A | N/A | Yes*
Biochemical Oxygen Demand | milligrams per litre | Weekly | 53 | 9 | 1160 | 30 | 32 | 50 | 85 | N/A | N/A | 60 | 1160 | Yes*
Total Suspended Solids | milligrams per litre | Weekly | 53 | 2 | 1130 | 50 | 74 | 55 | 187 | N/A | N/A | 70 | 1130 | Yes*
Chlorophyll a | micrograms per litre | Weekly | 53 | <1.0 | 5370 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | Monthly | 12 | <0.05 | 18.6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | milligrams per litre | Monthly | 12 | 10.7 | 19.9 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Oil and Grease | milligrams per litre | Monthly | 12 | <2 | 9 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | milligrams per litre | Monthly | 12 | 3.4 | 7.8 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
*The licensee is not taken to have exceeded a quality limit specified in this licence for pH, BOD or TSS if the licensee shows that the level of chlorophyll-a in the oxidation ponds during any exceedance was 100 ug/L or more (showing that the exceedance was caused by excessive algal growth).
VOLUME MONITORING
Annual Summary
1 April 2020 to 31 March 2021
Monitoring Point |  |  | Unit of | Sampling | No. of times measured during the year |  |  |  |  | Volume | Within
|  |  | Measurement | Frequency |  |  | Minimum | Mean | Maximum | Limit | Limits?
Point 1 - Discharge from the No.2 Oxidation Pond |  |  | kilolitres per day | Daily | 365 |  | 155 | 299 | 3636 | 2500 | No