## Kurri Kurri
KURRI KURRI WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - JULY 2020
|  | Environment Protection Licence No. 1767 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 3 August 2020 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 20 August 2020 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 2 |  | Site Description - In UV Disinfection Channel following UV Treatment
Site Code 5DE3005
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 July 2020 to 31 July 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | <2 | 3.8 | 2 | 10 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL | CFU/100mL | Monthly | MONTHLY | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 1.1 | 1.1 | 1.1 | 1.1 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 6.4 | 6.4 | 6.4 | 6.4 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Fortnightly | FORTNIGHTLY | 2 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly | WEEKLY | 5 | 7.09 | 7.266 | 7.3 | 7.35 | N/A | N/A | 6.5 - 8.5 | 7.09 - 7.35 | Yes
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | 0.065 | 0.137 | 0.095 | 0.33 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | <1 | 4 | 1 | 14 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 1 |  | Site Description - Pipe from No.3 Maturation Pond
Site Code 5OV1000
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 July 2020 to 31 July 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Daily during any Discharge |  | 1 | 25 | 25 | 25 | 25 | N/A | N/A | N/A | N/A | N/A
Chlorophyll a | Chlorophyll a | micrograms per litre | (ug/L) | Daily during any Discharge |  | 1 | 5.7 | 5.7 | 5.7 | 5.7 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Daily during any Discharge |  | 1 | 8.1 | 8.1 | 8.1 | 8.1 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Daily during any Discharge |  | 1 | 14.6 | 14.6 | 14.6 | 14.6 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Daily during any Discharge |  | 1 | 4 | 4 | 4 | 4 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Daily during any Discharge |  | 1 | 7.06 | 7.06 | 7.06 | 7.06 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Daily during any Discharge |  | 1 | 1.2 | 1.2 | 1.2 | 1.2 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Daily during any Discharge |  | 1 | 51 | 51 | 51 | 51 | N/A | N/A | N/A | N/A | N/A
*No samples were collected as no discharge occurred during the month
Note: For pollutants with less than four samples measured during the monthly period see below for interpretation of summary tables: One required sample for licence reporting: Min, Mean, Median and Max values are all the exact data point Two required samples for licence reporting: Min and Max values are the two exact data points Three required samples for licence reporting: Min, Median and Max values are the three exact data points
VOLUME MONITORING |  |  | 49
Monthly Summary
1 July 2020 to 31 July 2020
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
|  |  |  | Measurement |  | Frequency | [5 empty] | Limit
Point 1 - Pipe from No.3 Maturation Pond |  |  | 7 | kilolitres per day | 1128 | Daily | 31 |  | 0 | 43 | 1128 | N/A | N/A
Point 2 - In UV Disinfection Channel following UV Treatment |  |  | 4 | kilolitres per day | 23192 | Daily | 31 |  | 1741 | 6153 | 23192 | 38000 | Yes
Chlorophyll 'a'
Chlorophyll 'a'
Point 3 - Effluent Utilisation Pump
Point 4 - Pump Discharges from Dam to Williams River
Point 5 - Overflow Drain to Williams River
Note on D44: awebb: Last row of flow table