## Kurri Kurri
KURRI KURRI WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - OCTOBER 2020
|  | Environment Protection Licence No. 1767 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 2 November 2020 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 19 November 2020 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 2 |  | Site Description - In UV Disinfection Channel following UV Treatment
Site Code 5DE3005
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 October 2020 to 31 October 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <2 | 2.25 | 2 | 3 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL | CFU/100mL | Monthly | MONTHLY | 1 | ~7 | ~7 | ~7 | ~7 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 0.44 | 0.44 | 0.44 | 0.44 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 6.7 | 6.7 | 6.7 | 6.7 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Fortnightly | FORTNIGHTLY | 2 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly | WEEKLY | 4 | 7.15 | 7.365 | 7.41 | 7.49 | N/A | N/A | 6.5 - 8.5 | 7.15 - 7.49 | Yes
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 0.049 | 0.08725 | 0.075 | 0.15 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <1 | 2 | <1 | 5 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 1 |  | Site Description - Pipe from No.3 Maturation Pond
Site Code 5OV1000
[6 empty] | No. of times measured during the month for licence reporting * | Monthly Summary
1 October 2020 to 31 October 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Daily during any Discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Chlorophyll a | Chlorophyll a | micrograms per litre | (ug/L) | Daily during any Discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Daily during any Discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Daily during any Discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Daily during any Discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Daily during any Discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Daily during any Discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Daily during any Discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
*No samples were collected as no discharge occurred during the month
*No samples were collected as no discharge occurred during the month
Note: For pollutants with less than four samples measured during the monthly period see below for interpretation of summary tables: One required sample for licence reporting: Min, Mean, Median and Max values are all the exact data point Two required samples for licence reporting: Min and Max values are the two exact data points Three required samples for licence reporting: Min, Median and Max values are the three exact data points
VOLUME MONITORING |  |  | 49
Monthly Summary
1 October 2020 to 31 October 2020
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
|  |  |  | Measurement |  | Frequency | [5 empty] | Limit
Point 1 - Pipe from No.3 Maturation Pond |  |  | 7 | kilolitres per day | 0 | Daily | 31 |  | 0 | 0 | 0 | N/A | N/A
Point 2 - In UV Disinfection Channel following UV Treatment |  |  | 4 | kilolitres per day | 10561 | Daily | 31 |  | 3054 | 4750 | 12233 | 38000 | Yes
Chlorophyll 'a'
Chlorophyll 'a'
Point 3 - Effluent Utilisation Pump
Point 4 - Pump Discharges from Dam to Williams River
Point 5 - Overflow Drain to Williams River
Note on D48: awebb: Last row of flow table