## Morpeth
MORPETH WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - FEBRUARY 2020
|  | Environment Protection Licence No. 10693 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 4 March 2020 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 19 March 2020 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 |  | Site Description - Pipe from the disinfected effluent chamber to the Hunter River
Site Code 5DE1303
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2020 to 29 February 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 3 | 4.75 | 4.5 | 7 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Monthly | MONTHLY | 1 | ~17 | 2979 | 449 | ~11000 | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 4.2 | 4.2 | 4.2 | 4.2 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 0.11 | 0.11 | 0.11 | 0.11 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Fortnightly | FORTNIGHTLY | 2 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly | WEEKLY | 4 | 7.38 | 7.63 | 7.645 | 7.85 | N/A | N/A | 6.5 - 8.5 | 7.38 - 7.85 | Yes
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 0.15 | 0.15 | 0.15 | 0.15 | N/A | N/A | N/A | N/A | N/A
Total Kjeldahl Nitrogen | TKN | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 5.6 | 5.6 | 5.6 | 5.6 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 2 | 5 | 5.5 | 7 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 4 |  | Site Description - Pipe from the Effluent Pump Station to the Hunter River
Site Code 5PF1000
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2020 to 29 February 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Special Frequency 1 |  | 3 | 21 | 31 | 21 | 52 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Special Frequency 1 |  | 3 | 250000 | 3016667 | 1500000 | 7300000 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Special Frequency 1 |  | 3 | 3.9 | 8.6 | 4.7 | 17.3 | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Special Frequency 1 |  | 3 | 1.5 | 4.5 | 2.8 | 9.1 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Special Frequency 1 |  | 3 | 3 | 5 | 3 | 8 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Special Frequency 1 |  | 3 | 1.3 | 1.9 | 1.6 | 2.7 | N/A | N/A | N/A | N/A | N/A
Total Kjeldahl Nitrogen | TKN | milligrams per litre | (mg/L) | Special Frequency 1 |  | 3 | 6.7 | 14.6 | 14.8 | 22.2 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Special Frequency 1 |  | 3 | 36 | 94 | 106 | 141 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Special Frequency 1 |  | 3 | 7.1 | 7.29 | 7.27 | 7.51 | N/A | N/A | N/A | N/A | N/A
VOLUME MONITORING |  |  | 54
Monthly Summary
1 February 2020 to 29 February 2020
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  |  | Volume | Within Limits
|  |  |  | Measurement |  | Frequency |  |  | Maximum | Limit
Point 1 - Pipe from the Disinfected Effluent Chamber to the Hunter River |  |  | 3 | kilolitres per day | 33.08 | Daily | 29 |  | 33080 | 208000 | Yes
Point 3 - Maturation Pond Flow |  |  | 4 | kilolitres per day | 2 | Daily | 29 |  | 2000 | N/A | N/A
Point 4 - Pumped Discharge to Hunter River |  |  | 6 | kilolitres per day | 26.9 | Daily | 29 |  | 26900 | 208000 | Yes
Point 5 - Effluent Pump Station Overflow to Maturation Pond |  |  | 7 | kilolitres per day | 0 | Daily | 29 |  | 0 | N/A | N/A
Combined Point 1 and 4 |  |  | 8 | kilolitres per day | 54.59 | Daily | 29 |  | 54590 | 208000 | Yes
Note on D45: awebb: Last row of flow table