## Morpeth
MORPETH WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - JUNE 2020
|  | Environment Protection Licence No. 10693 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 1 July 2020 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 20 July 2020 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 |  | Site Description - Pipe from the disinfected effluent chamber to the Hunter River
Site Code 5DE1303
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 June 2020 to 30 June 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 2 | 2.5 | 2.5 | 3 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Monthly | MONTHLY | 1 | <17 | <17 | <17 | <17 | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 5.2 | 5.2 | 5.2 | 5.2 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Fortnightly | FORTNIGHTLY | 2 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly | WEEKLY | 4 | 7.13 | 7.4525 | 7.545 | 7.59 | N/A | N/A | 6.5 - 8.5 | 7.13 - 7.59 | Yes
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 0.22 | 0.22 | 0.22 | 0.22 | N/A | N/A | N/A | N/A | N/A
Total Kjeldahl Nitrogen | TKN | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 1.2 | 1.2 | 1.2 | 1.2 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <1 | 2.5 | 2 | 5 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 4 |  | Site Description - Pipe from the Effluent Pump Station to the Hunter River
Site Code 5PF1000
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 June 2020 to 30 June 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Special Frequency 1 |  | 2 | 21 | 29 | 29 | 37 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Special Frequency 1 |  | 2 | 340000 | 390000 | 390000 | 440000 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Special Frequency 1 |  | 2 | 5.5 | 5.65 | 5.65 | 5.8 | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Special Frequency 1 |  | 2 | 1.4 | 1.85 | 1.85 | 2.3 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Special Frequency 1 |  | 2 | 44 | 66 | 66 | 88 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Special Frequency 1 |  | 2 | 0.59 | 1.395 | 1.395 | 2.2 | N/A | N/A | N/A | N/A | N/A
Total Kjeldahl Nitrogen | TKN | milligrams per litre | (mg/L) | Special Frequency 1 |  | 2 | 8 | 8.2 | 8.2 | 8.4 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Special Frequency 1 |  | 2 | 24 | 55 | 55 | 86 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Special Frequency 1 |  | 2 | 7.11 | 7.195 | 7.195 | 7.28 | N/A | N/A | N/A | N/A | N/A
VOLUME MONITORING |  |  | 54
Monthly Summary
1 June 2020 to 30 June 2020
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  |  | Volume | Within Limits
|  |  |  | Measurement |  | Frequency |  |  | Maximum | Limit
Point 1 - Pipe from the Disinfected Effluent Chamber to the Hunter River |  |  | 3 | kilolitres per day | 27.94 | Daily | 30 |  | 27940 | 208000 | Yes
Point 3 - Maturation Pond Flow |  |  | 4 | kilolitres per day | 0 | Daily | 30 |  | 0 | N/A | N/A
Point 4 - Pumped Discharge to Hunter River |  |  | 6 | kilolitres per day | 4.48 | Daily | 30 |  | 4480 | 208000 | Yes
Point 5 - Effluent Pump Station Overflow to Maturation Pond |  |  | 7 | kilolitres per day | 0 | Daily | 30 |  | 0 | N/A | N/A
Combined Point 1 and 4 |  |  | 8 | kilolitres per day | 32.42 | Daily | 30 |  | 32420 | 208000 | Yes
Note on D45: awebb: Last row of flow table