## Morpeth
MORPETH WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - JULY 2021
|  | Environment Protection Licence No. 10693 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 2 August 2021 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 19 August 2021 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 |  | Site Description - Pipe from the disinfected effluent chamber to the Hunter River
Site Code 5DE1303
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 July 2021 to 31 July 2021
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 3 | 3.5 | 3.5 | 4 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Monthly | MONTHLY | 1 | <17 | <17 | <17 | <17 | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 6.14 | 6.14 | 6.14 | 6.14 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Fortnightly | FORTNIGHTLY | 2 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly | WEEKLY | 4 | 7.41 | 7.49 | 7.51 | 7.53 | N/A | N/A | 6.5 - 8.5 | 7.41 - 7.53 | Yes
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 0.2 | 0.2 | 0.2 | 0.2 | N/A | N/A | N/A | N/A | N/A
Total Kjeldahl Nitrogen | TKN | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 1.3 | 1.3 | 1.3 | 1.3 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <1 | 3.25 | 3 | 6 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 4 |  | Site Description - Pipe from the Effluent Pump Station to the Hunter River
Site Code 5PF1000
[6 empty] | No. of times measured during the month for licence reporting * | Monthly Summary
1 July 2021 to 31 July 2021
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Kjeldahl Nitrogen | TKN | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Special Frequency 1 |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
*No samples were collected as no discharge occurred during the month
Note: For pollutants with less than four samples measured during the monthly period see below for interpretation of summary tables: One required sample for licence reporting: Min, Mean, Median and Max values are all the exact data point Two required samples for licence reporting: Min and Max values are the two exact data points Three required samples for licence reporting: Min, Median and Max values are the three exact data points
VOLUME MONITORING |  |  | 54
Monthly Summary
1 July 2021 to 31 July 2021
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
|  |  |  | Measurement |  | Frequency | [5 empty] | Limit
Point 1 - Pipe from the Disinfected Effluent Chamber to the Hunter River |  |  | 3 | kilolitres per day | 30.52 | Daily | 31 |  | 6330 | 9933.2258 | 13330 | 208000 | Yes
Point 3 - Maturation Pond Flow |  |  | 4 | kilolitres per day | 0 | Daily | 31 |  | 0 | 0 | 0 | N/A | N/A
Point 4 - Pumped Discharge to Hunter River |  |  | 6 | kilolitres per day | 7.89 | Daily | 31 |  | 0 | 0 | 0 | 208000 | Yes
Point 5 - Effluent Pump Station Overflow to Maturation Pond |  |  | 7 | kilolitres per day | 0 | Daily | 31 |  | 0 | 0 | 0 | N/A | N/A
Combined Point 1 and 4 |  |  | 8 | kilolitres per day | 38.41 | Daily | 31 |  | 6330 | 9933.2258 | 13330 | 208000 | Yes
Note on D50: awebb: Last row of flow table