## Morpeth
MORPETH WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - JULY 2022
|  | Environment Protection Licence No. 10693 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 1 August 2022 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 19 August 2022 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 |  | Site Description - Pipe from the disinfected effluent chamber to the Hunter River
Site Code 5DE1303
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 July 2022 to 31 July 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 3 | 12.25 | 13 | 20 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Monthly | MONTHLY | 1 | 7900 | 7900 | 7900 | 7900 | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 1.91 | 1.91 | 1.91 | 1.91 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 0.52 | 0.52 | 0.52 | 0.52 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Fortnightly | FORTNIGHTLY | 2 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly | WEEKLY | 4 | 7.12 | 7.33 | 7.325 | 7.55 | N/A | N/A | 6.5 - 8.5 | 7.12 - 7.55 | Yes
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 1.57 | 1.57 | 1.57 | 1.57 | N/A | N/A | N/A | N/A | N/A
Total Kjeldahl Nitrogen | TKN | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 3.9 | 3.9 | 3.9 | 3.9 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 3 | 29 | 25 | 63 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 4 |  | Site Description - Pipe from the Effluent Pump Station to the Hunter River
Site Code 5PF1000
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 July 2022 to 31 July 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Special Frequency 1 |  | 2 | 12 | 41.5 | 41.5 | 71 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Special Frequency 1 |  | 2 | 150000 | 445000 | 445000 | 740000 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Special Frequency 1 |  | 2 | 1.27 | 3.605 | 3.605 | 5.94 | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Special Frequency 1 |  | 2 | 1.97 | 2.22 | 2.22 | 2.47 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Special Frequency 1 |  | 2 | <2 | 7 | 7 | 12 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Special Frequency 1 |  | 2 | 1 | 1.495 | 1.495 | 1.99 | N/A | N/A | N/A | N/A | N/A
Total Kjeldahl Nitrogen | TKN | milligrams per litre | (mg/L) | Special Frequency 1 |  | 2 | 4.5 | 9.2 | 9.2 | 13.9 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Special Frequency 1 |  | 2 | 35 | 104.5 | 104.5 | 174 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Special Frequency 1 |  | 2 | 7.05 | 7.07 | 7.07 | 7.09 | N/A | N/A | N/A | N/A | N/A
Note: For pollutants with less than four samples measured during the monthly period see below for interpretation of summary tables: One required sample for licence reporting: Min, Mean, Median and Max values are all the exact data point Two required samples for licence reporting: Min and Max values are the two exact data points Three required samples for licence reporting: Min, Median and Max values are the three exact data points
VOLUME MONITORING |  |  | 54
Monthly Summary
1 July 2022 to 31 July 2022
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
|  |  |  | Measurement |  | Frequency | [5 empty] | Limit
Point 1 - Pipe from the Disinfected Effluent Chamber to the Hunter River |  |  | 3 | kilolitres per day | 30.52 | Daily | 31 |  | 7810 | 16739.5484 | 46360 | 208000 | Yes
Point 3 - Maturation Pond Flow |  |  | 4 | kilolitres per day | 0 | Daily | 31 |  | 0 | 191.6129 | 2161 | N/A | N/A
Point 4 - Pumped Discharge to Hunter River |  |  | 6 | kilolitres per day | 7.89 | Daily | 31 |  | 0 | 21207.7742 | 116241 | 208000 | Yes
Point 5 - Effluent Pump Station Overflow to Maturation Pond |  |  | 7 | kilolitres per day | 0 | Daily | 31 |  | 0 | 0 | 0 | N/A | N/A
Combined Point 1 and 4 |  |  | 8 | kilolitres per day | 38.41 | Daily | 31 |  | 7810 | 37947.3226 | 162601 | 208000 | Yes
*Two discharge events occurred during reporting period with one sample not measured
0
Note on D50: awebb: Last row of flow table