## Morpeth
MORPETH WASTEWATER TREATMENT WORKS - ANNUAL POLLUTION MONITORING SUMMARY - 2020-21
| Environment Protection Licence No. 10693 |  |  |  |  | Licensee | Hunter Water Corporation
| Date Obtained: 7 April 2021 | [5 empty] | 36 Honeysuckle Drive
| Date Published: 23 April 2021 | [5 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 | Site Description - Pipe from the Disinfected effluent chamber to the Hunter River
Site Code 5DE1303
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 April 2020 to 31 March 2021
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Weekly | 53 | <2 | 25 | N/A | N/A | 10 | 8 | N/A | N/A | N/A | N/A | Yes
Faecal Coliforms | colony forming units per 100 mL | Monthly | 12 | <17 | 830 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | Monthly | 12 | <0.05 | 0.72 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | milligrams per litre | Monthly | 12 | 2 | 6.2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Oil and Grease | milligrams per litre | Fortnightly | 26 | <2 | 5 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | milligrams per litre | Monthly | 12 | 0.16 | 1.9 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Kjeldahl Nitrogen | milligrams per litre | Monthly | 12 | 0.3 | 2.3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | Weekly | 53 | <1 | 46 | N/A | N/A | 20 | 12.6 | N/A | N/A | N/A | N/A | Yes
pH | pH | Weekly | 53 | 7.13 | 8.01 | N/A | N/A | N/A | N/A | N/A | N/A | 6.5 - 8.5 | 7.13 - 8.01 | Yes
EPA Id. No. 4 | Site Description - Pipe from the Effluent Pump Station to the Hunter River
Site Code 5PF1000
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 April 2020 to 31 March 2021
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Special Frequency 1 | 19 | 10 | 194 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | colony forming units per 100 mL | Special Frequency 1 | 19 | ~80000 | 6800000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | Special Frequency 1 | 19 | 0.9 | 18.8 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | milligrams per litre | Special Frequency 1 | 19 | <0.05 | 4.2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Oil and Grease | milligrams per litre | Special Frequency 1 | 19 | <1 | 88 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | milligrams per litre | Special Frequency 1 | 19 | 0.46 | 3.9 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Kjeldahl Nitrogen | milligrams per litre | Special Frequency 1 | 19 | 3.1 | 28 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | Special Frequency 1 | 19 | 8 | 232 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH | pH | Special Frequency 1 | 19 | 6.93 | 7.98 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
VOLUME MONITORING
Annual Summary
1 April 2020 to 31 March 2021
Monitoring Point |  |  | Unit of | Sampling | No. of times measured during the year |  |  |  |  | Volume | Within
|  |  | Measurement | Frequency |  |  | Minimum | Mean | Maximum | Limit | Limits?
Point 1 - Pipe from the Disinfected Effluent Chamber to the Hunter River |  |  | kilolitres per day | Daily | 365 |  | 4910 | 12128 | 42330 | 208000 | Yes
Point 3 - Maturation Pond Flow |  |  | kilolitres per day | Daily | 365 |  | 0 | 258 | 2180 | N/A | N/A
Point 4 - Pumped Discharge to Hunter River |  |  | kilolitres per day | Daily | 365 |  | 0 | 1592 | 63167 | 208000 | Yes
Point 5 - Effluent Pump Station Overflow to Maturation Pond |  |  | kilolitres per day | Daily | 365 |  | 0 | 68 | 12500 | N/A | N/A
Combined Point 1 and 4 |  |  | kilolitres per day | Daily | 365 |  | 4910 | 13719 | 86067 | 208000 | Yes