## Morpeth
MORPETH WASTEWATER TREATMENT WORKS - ANNUAL POLLUTION MONITORING SUMMARY - 2021-2022
| Environment Protection Licence No. 10693 |  |  |  |  | Licensee | Hunter Water Corporation
| Date Obtained: 4 April 2022 | [5 empty] | 36 Honeysuckle Drive
| Date Published: 26 April 2022 | [5 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 | Site Description - Pipe from the Disinfected effluent chamber to the Hunter River
Site Code 5DE1303
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 April 2021 to 31 March 2022
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Weekly | 52 | <2 | 19 | N/A | N/A | 10 | 8 | N/A | N/A | N/A | N/A | Yes
Faecal Coliforms | colony forming units per 100 mL | Monthly | 12 | <17 | 7500 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | Monthly | 12 | <0.05 | 2.23 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | milligrams per litre | Monthly | 12 | 2.64 | 7.62 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Oil and Grease | milligrams per litre | Fortnightly | 26 | <2 | 2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | milligrams per litre | Monthly | 12 | 0.13 | 1.12 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Kjeldahl Nitrogen | milligrams per litre | Monthly | 12 | 0.9 | 3.6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | Weekly | 52 | <1 | 32 | N/A | N/A | 20 | 10 | N/A | N/A | N/A | N/A | Yes
pH | pH | Weekly | 52 | 6.98 | 7.85 | N/A | N/A | N/A | N/A | N/A | N/A | 6.5 - 8.5 | 6.98 - 7.85 | Yes
EPA Id. No. 4 | Site Description - Pipe from the Effluent Pump Station to the Hunter River
Site Code 5PF1000
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 April 2021 to 31 March 2022
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Special Frequency 1 | 20 | 12 | 154 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | colony forming units per 100 mL | Special Frequency 1 | 20 | 5800 | 960000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | Special Frequency 1 | 20 | 1.89 | 25.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | milligrams per litre | Special Frequency 1 | 20 | 0.82 | 4.42 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Oil and Grease | milligrams per litre | Special Frequency 1 | 20 | <2 | 98 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | milligrams per litre | Special Frequency 1 | 20 | 0.3 | 3.88 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Kjeldahl Nitrogen | milligrams per litre | Special Frequency 1 | 20 | 3.8 | 31.3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | Special Frequency 1 | 20 | 22 | 348 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH | pH | Special Frequency 1 | 20 | 7.02 | 7.43 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
VOLUME MONITORING
Annual Summary
1 April 2021 to 31 March 2022
Monitoring Point |  |  | Unit of | Sampling | No. of times measured during the year |  |  |  |  | Volume | Within
|  |  | Measurement | Frequency |  |  | Minimum | Mean | Maximum | Limit | Limits?
Point 1 - Pipe from the Disinfected Effluent Chamber to the Hunter River |  |  | kilolitres per day | Daily | 365 |  | 5200 | 12576 | 40090 | 208000 | Yes
Point 3 - Maturation Pond Flow |  |  | kilolitres per day | Daily | 365 |  | 0 | 20 | 6936 | N/A | N/A
Point 4 - Pumped Discharge to Hunter River |  |  | kilolitres per day | Daily | 365 |  | 0 | 1238 | 61316 | 208000 | Yes
Point 5 - Effluent Pump Station Overflow to Maturation Pond |  |  | kilolitres per day | Daily | 365 |  | 0 | 518 | 48484 | N/A | N/A
Combined Point 1 and 4 |  |  | kilolitres per day | Daily | 365 |  | 5200 | 13814 | 84427 | 208000 | Yes