## Paxton
PAXTON WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - JANUARY 2020
|  | Environment Protection Licence No. 3755 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 4 February 2020 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 20 February 2020 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 3 |  | Site Description - Effluent Discharge Chamber
Site Code 5PA2805
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 January 2020 to 31 January 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | <2 | <2 | 2 | 2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Cond (EPA) | Millisemens per centimetre | (mS/cm) | Weekly | WEEKLY | 5 | 0.802 | 0.819 | 0.821 | 0.835 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | 0.06 | 0.124 | 0.1 | 0.28 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | 7 | 8 | 7.7 | 9 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | 0.077 | 0.1092 | 0.096 | 0.15 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | Tss(b) | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | <1 | 2 | 2 | 3 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly | WEEKLY | 5 | 7.46 | 7.512 | 7.48 | 7.66 | N/A | N/A | 6.5 - 8.5 | 7.46 - 7.66 | Yes
EPA Id. No. 4 |  | Site Description - Overflow weir from Wet Weather Storage Pond
Site Code 5OV1400
[6 empty] | No. of times measured during the month for licence reporting* | Monthly Summary
1 January 2020 to 31 January 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | Chlorophyll 'a' | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
*No samples were collected as no discharge occurred during the month
VOLUME MONITORING |  |  | 44
Monthly Summary
1 January 2020 to 31 January 2020
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  |  | Volume | Within Limits
|  |  |  | Measurement |  | Frequency |  |  | Maximum | Limit
Point 3 - Effluent Discharge Chamber |  |  | 4 | kilolitres per day | 0.361 | Daily | 31 |  | 361 | 1100 | Yes
Point 4 - Overflow weir from Wet Weather Storage Pond |  |  | 7 | kilolitres per day | 0 | Daily | 31 |  | 0 | 1100 | Yes
Combined Point 3 and 4 |  |  | 8 | kilolitres per day | 0.361 | Daily | 31 |  | 361 | 1,100** | Yes
**As per EPL condition L4.3, the licensee may discharge a combined volume of up to 3,000 kL/day from Points 3 and 4 during wet weather. Wet weather is total rainfall recorded at the rain gauge at the premises, over a period of three consecutive days, is equal to or greater than 10 mm.
Chlorophyll 'a'
Chlorophyll 'a'
Chlorophyll 'a'
Point 3 - Effluent Utilisation Pump
Point 4 - Pump Discharges from Dam to Williams River
Point 5 - Overflow Drain to Williams River
Note on D37: awebb: Last row of flow table