## Paxton
PAXTON WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - NOVEMBER 2025
|  | Environment Protection Licence No. 3755 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 1 December 2025 | [7 empty] | 36 Honeysuckle Drive
Date Published: 19 December 2025 |  | Date Published: 19 December 2025 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 3 |  | Site Description - Final Effluent Discharge Chamber at Final Effluent Tank at Treatment Plant
Site Code 5PA2805
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 November 2025 to 30 November 2025
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Cond (EPA) | Millisemens per centimetre | (mS/cm) | Weekly | WEEKLY | 4 | 0.773 | 0.78775 | 0.7895 | 0.799 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <0.05 | 0.1075 | 0.095 | 0.19 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 5.52 | 6.01 | 5.96 | 6.6 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 0.024 | 0.03325 | 0.0335 | 0.042 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | Tss(b) | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <1 | 2 | 2 | 3 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly | WEEKLY | 4 | 7.34 | 7.42 | 7.435 | 7.47 | N/A | N/A | 6.5 - 8.5 | 7.34 - 7.47 | Yes
EPA Id. No. 4 |  | Site Description - Overflow Weir from Wet Weather Storage Pond
Site Code 5OV1400
[6 empty] | No. of times measured during the month for licence reporting* | Monthly Summary
1 November 2025 to 30 November 2025
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | Chlorophyll 'a' | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
*No samples were collected as no discharge occurred during the month
VOLUME MONITORING |  |  | 45
Monthly Summary
1 November 2025 to 30 November 2025
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
|  |  |  | Measurement |  | Frequency | [5 empty] | Limit
Point 3 - Effluent Discharge Chamber |  |  | 4 | kilolitres per day | 0.7548 | Continuous | 30 |  | 377.7 | 431.9533 | 525.7 | 1,100** | Yes
Point 4 - Overflow Weir from Wet Weather Storage Pond |  |  | 7 | kilolitres per day | 0 | Continuous | 30 |  | 0 | 0 | 0 | 1,100** | Yes
Combined Point 3 and 4 |  |  | 8 | kilolitres per day | 0.7548 | Continuous | 30 |  | 377.7 | 431.9533 | 525.7 | 1,100** | Yes
**As per EPL condition L4.3, the licensee may discharge a combined volume of up to 3,000 kL/day from Points 3 and 4 during wet weather. Wet weather is total rainfall recorded at the rain gauge at the premises, over a period of three consecutive days, is equal to or greater than 10 mm.
Chlorophyll 'a'
Chlorophyll 'a'
Chlorophyll 'a'
Point 3 - Effluent Utilisation Pump
Point 4 - Pump Discharges from Dam to Williams River
Point 5 - Overflow Drain to Williams River
15500
N/A
N/A
Note on D37: awebb: Last row of flow table