## Paxton
PAXTON WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - FEBRUARY 2026
|  | Environment Protection Licence No. 3755 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 2 March 2026 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 19 March 2026 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 3 |  | Site Description - Final Effluent Discharge Chamber at Final Effluent Tank at Treatment Plant
Site Code 5PA2805
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2026 to 28 February 2026
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <2 | <2 | <2 | 2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Cond (EPA) | Millisemens per centimetre | (mS/cm) | Weekly | WEEKLY | 4 | 0.674 | 0.712 | 0.72 | 0.734 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <0.05 | 0.0525 | <0.05 | 0.06 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 5.54 | 6.33 | 6.065 | 7.65 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 0.033 | 0.075 | 0.0715 | 0.124 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | Tss(b) | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <1 | 2 | 2 | 3 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly | WEEKLY | 4 | 7.33 | 7.41 | 7.41 | 7.49 | N/A | N/A | 6.5 - 8.5 | 7.33 - 7.49 | Yes
EPA Id. No. 4 |  | Site Description - Overflow Weir from Wet Weather Storage Pond
Site Code 5OV1400
[6 empty] | No. of times measured during the month for licence reporting* | Monthly Summary
1 February 2026 to 28 February 2026
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | Chlorophyll 'a' | milligrams per litre | (mg/L) | First 24hrs then weekly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
*No samples were collected as no discharge occurred during the month
VOLUME MONITORING |  |  | 45
Monthly Summary
1 February 2026 to 28 February 2026
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
|  |  |  | Measurement |  | Frequency | [5 empty] | Limit
Point 3 - Effluent Discharge Chamber |  |  | 4 | kilolitres per day | 0.7548 | Continuous | 28 |  | 394 | 436.6714 | 528.5 | 1,100** | Yes***
Point 4 - Overflow Weir from Wet Weather Storage Pond |  |  | 7 | kilolitres per day | 0 | Continuous | 28 |  | 0 | 0 | 0 | 1,100** | Yes
Combined Point 3 and 4 |  |  | 8 | kilolitres per day | 0.7548 | Continuous | 28 |  | 394 | 436.6714 | 528.5 | 1,100** | Yes***
**As per EPL condition L4.3, the licensee may discharge a combined volume of up to 3,000 kL/day from Points 3 and 4 during wet weather. Wet weather is total rainfall recorded at the rain gauge at the premises, over a period of three consecutive days, is equal to or greater than 10 mm.
*** Onsite Weather Station Appears to have been broken during wet weather event that had flows over the 1,100 limit nearby rainfall data for the area had rainfall of greater than the required amount during discharge of above 1,100 kL
Chlorophyll 'a'
Chlorophyll 'a'
Chlorophyll 'a'
Point 3 - Effluent Utilisation Pump
Point 4 - Pump Discharges from Dam to Williams River
Point 5 - Overflow Drain to Williams River
15500
N/A
N/A
Note on D37: awebb: Last row of flow table