## Paxton
PAXTON WASTEWATER TREATMENT WORKS - ANNUAL POLLUTION MONITORING SUMMARY - 2020-21
| Environment Protection Licence No. 3755 |  |  |  |  | Licensee | Hunter Water Corporation
| Date Obtained: 7 April 2021 | [5 empty] | 36 Honeysuckle Drive
| Date Published: 23 April 2021 | [5 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 3 | Site Description - Final Effluent Discharge Chamber at Final Effluent Tank at Treatment Plant
Site Code 5PA2805
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 April 2020 to 31 March 2021
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Weekly | 53 | <2 | 11 | 6 | <2 | 10 | 3 | N/A | N/A | N/A | N/A | Yes
Conductivity | millisiemens per centimetre | Weekly | 53 | 0.538 | 0.995 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | Weekly | 53 | <0.05 | 28.6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | milligrams per litre | Weekly | 53 | 3.7 | 36.5 | 8 | 6.1 | 15 | 10.2 | N/A | N/A | N/A | N/A | Yes
Phosphorus (total) | milligrams per litre | Weekly | 53 | 0.011 | 0.35 | 0.3 | 0.035 | 1 | 0.118 | N/A | N/A | N/A | N/A | Yes
Total Suspended Solids | milligrams per litre | Weekly | 53 | <1 | 7 | 10 | <1 | 15 | 3 | N/A | N/A | N/A | N/A | Yes
pH | pH | Weekly | 53 | 6.92 | 7.95 | N/A | N/A | N/A | N/A | N/A | N/A | 6.5 - 8.5 | 6.92 - 7.95 | Yes
EPA Id. No. 4 | Site Description - Overflow Weir from Wet Weather Storage Pond
Site Code 5OV1400
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 April 2020 to 31 March 2021
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | First 24hrs then weekly | 2 | 7 | 19 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Yes
Faecal Coliforms | col/100mL | First 24hrs then weekly | 2 | 32000 | ~1300000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Yes
Total Suspended Solids | milligrams per litre | First 24hrs then weekly | 2 | 14 | 60 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Yes
VOLUME MONITORING
Annual Summary
1 April 2020 to 31 March 2021
|  |  | Unit of | Sampling | No. of times measured during the year |  |  |  |  | Volume | Within
Monitoring Point |  |  | Measurement | Frequency |  |  | Minimum | Mean | Maximum | Limit | Limits?
Point 3 - Final Effluent Discharge Chamber at Final Effluent Tank at Treatment Plant |  |  | kilolitres per day | Daily | 365 |  | 91 | 457 | 2122 | 1100 | No
Point 4 - Overflow Weir from Wet Weather Storage Pond |  |  | kilolitres per day | Daily | 365 |  | 0 | 14 | 1170 | 1100 | No
Combined Point 3 and 4 |  |  | kilolitres per day | Daily | 365 |  | 91 | 471 | 3250 | 1100 | No
Note: As per EPL condition L4.3, the licensee may discharge a combined volume of up to 3,000 kL/day from Points 3 and 4 during wet weather. Wet weather is total rainfall recorded at the rain gauge at the premises, over a period of three consecutive days, is equal to or greater than 10 mm.