## Raymond Terrace
RAYMOND TERRACE WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - APRIL 2022
|  | Environment Protection Licence No. 217 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 2 May 2022 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 19 May 2022 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 2 |  | Site Description - At the discharge point at UV Disinfection
Site Code 5DE1500
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 April 2022 to 30 April 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <2 | <2 | <2 | 2 | N/A | N/A | 30 | 2 | Yes
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Weekly | WEEKLY | 4 | 1 | 101 | 21.5 | ~360 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 1.63 | 2.2875 | 2.295 | 2.93 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 2.13 | 3.0125 | 3.14 | 3.64 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Fortnightly | FORTNIGHTLY | 2 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 0.44 | 0.565 | 0.575 | 0.67 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 1 | 2.5 | 2 | 5 | N/A | N/A | 30 | 5 | Yes
pH | pH | pH | pH | Weekly | WEEKLY | 4 | 7.26 | 7.3275 | 7.315 | 7.42 | N/A | N/A | 6.5 - 8.5 | 7.26 - 7.42 | Yes
EPA Id. No. 1 |  | Site Description - At the discharge from the No.2 Maturation Pond
Site Code 5OV1500
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 April 2022 to 30 April 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Daily during any Discharge |  | 20 | 6 | 9.35 | 9.5 | 13 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Daily during any Discharge |  | 20 | 0.13 | 2.5875 | 2.615 | 4.91 | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Daily during any Discharge |  | 20 | 0.3 | 0.4185 | 0.43 | 0.6 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Daily during any Discharge |  | 20 | 3.7 | 5.8335 | 5.84 | 8.75 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Daily during any Discharge |  | 20 | <2 | 2.1 | <2 | 4 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Daily during any Discharge |  | 20 | 0.92 | 1.167 | 1.165 | 1.41 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Daily during any Discharge |  | 20 | 3 | 24.2 | 25.5 | 36 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Daily during any Discharge |  | 20 | 7.25 | 8.5535 | 8.76 | 10.1 | N/A | N/A | N/A | N/A | N/A
Note: For pollutants with less than four samples measured during the monthly period see below for interpretation of summary tables: One required sample for licence reporting: Min, Mean, Median and Max values are all the exact data point Two required samples for licence reporting: Min and Max values are the two exact data points Three required samples for licence reporting: Min, Median and Max values are the three exact data points
VOLUME MONITORING |  |  | 50
Monthly Summary
1 April 2022 to 30 April 2022
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
|  |  |  | Measurement |  | Frequency | [5 empty] | Limit
Point 1 - At the discharge from the No.2 Maturation Pond |  |  | 7 | kilolitres per day | 0 | Daily | 30 |  | 0 | 2097 | 14690 | N/A | N/A
Point 2 - At the discharge point at UV Disinfection |  |  | 3 | kilolitres per day | 12958 | Daily | 30 |  | 8089 | 11128.8333 | 12615 | 90000 | Yes
Chlorophyll 'a'
Chlorophyll 'a'
Point 3 - Effluent Utilisation Pump
Point 4 - Pump Discharges from Dam to Williams River
Point 5 - Overflow Drain to Williams River
Note on D48: awebb: Last row of flow table