## Raymond Terrace
RAYMOND TERRACE WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - AUGUST 2026
|  | Environment Protection Licence No. 217 | [7 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 1 September 2026 | [8 empty] | 36 Honeysuckle Drive
|  | Date Published: 21 September 2026 | [8 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 2 |  | Site Description - At the discharge point at UV Disinfection
Site Code 5DE1500
[7 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | (mg/L) | Weekly | WEEKLY | 4 | <2 | 2.5 | 2.5 | 3 | N/A | N/A | 30 | 3 | Yes
Faecal Coliforms | FC Hdn | colony forming units per 100 mL |  | CFU/100mL | Weekly | WEEKLY | 4 | <2 | 7.5 | 3 | 22 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | (mg/L) | Weekly | WEEKLY | 4 | 0.08 | 0.16 | 0.155 | 0.25 | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | TON | milligrams per litre |  | (mg/L) | Weekly | WEEKLY | 4 | 1.95 | 2.125 | 2.06 | 2.43 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | (mg/L) | Weekly | WEEKLY | 4 | 2.94 | 3.4 | 3.405 | 3.85 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre |  | (mg/L) | Fortnightly | FORTNIGHTLY | 2 | <2 | 2.5 | 2.5 | 3 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | (mg/L) | Weekly | WEEKLY | 4 | 0.25 | 0.455 | 0.425 | 0.72 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | (mg/L) | Weekly | WEEKLY | 4 | <1 | 3.25 | 3.5 | 5 | N/A | N/A | 30 | 5 | Yes
pH | pH | pH |  | pH | Weekly | WEEKLY | 4 | 7.37 | 7.4575 | 7.455 | 7.55 | N/A | N/A | 6.5 - 8.5 | 7.37 - 7.55 | Yes
EPA Id. No. 1 |  | Site Description - At the discharge from the No.2 Maturation Pond
Site Code 5OV1500
[7 empty] | No. of times measured during the month for licence reporting* | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | (mg/L) | Daily during any Discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | (mg/L) | Daily during any Discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | TON | milligrams per litre |  | (mg/L) | Daily during any Discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | (mg/L) | Daily during any Discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre |  | (mg/L) | Daily during any Discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | (mg/L) | Daily during any Discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | (mg/L) | Daily during any Discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH |  | pH | Daily during any Discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
* No samples were collected as no discharge occurred during the month
Note: For pollutants with less than four samples measured during the monthly period see below for interpretation of summary tables: One required sample for licence reporting: Min, Mean, Median and Max values are all the exact data point Two required samples for licence reporting: Min and Max values are the two exact data points Three required samples for licence reporting: Min, Median and Max values are the three exact data points
VOLUME MONITORING |  |  |  | 54
Monthly Summary
1 August 2026 to 31 August 2026
Monitoring Point |  |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
[5 empty] | Measurement |  | Frequency | [5 empty] | Limit
Point 1 - At the discharge from the No.2 Maturation Pond |  |  | 0 | 7 | kilolitres per day | 0 | Continuous | 31 |  | 0 | 0 | 0 | N/A | N/A
Point 2 - At the discharge point at UV Disinfection |  |  | 0 | 3 | kilolitres per day | 12958 | Continuous | 31 |  | 5102 | 5694.5806 | 6455 | 90000 | Yes
31
Chlorophyll 'a'
Chlorophyll 'a'
Point 3 - Effluent Utilisation Pump
Point 4 - Pump Discharges from Dam to Williams River
Point 5 - Overflow Drain to Williams River
15500
N/A
N/A
Note on E48: awebb: Last row of flow table