## Raymond Terrace
RAYMOND TERRACE WASTEWATER TREATMENT WORKS - ANNUAL POLLUTION MONITORING SUMMARY - 2020-21
| Environment Protection Licence No. 217 |  |  |  | Hunter Water Corporation
| Date Obtained: 5 October 2021 |  |  |  | 36 Honeysuckle Drive
| Date Published: 25 October 2021 |  |  |  | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 | Site Description - At the discharge from the No.2 Maturation Pond
Site Code 5OV1500
|  |  | No. of times measured during the year for licence reporting* | Annual Summary
1 October 2020 - 30 September 2021
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Daily during any Discharge | 16 | <2 | 12 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | Daily during any Discharge | 16 | 0.12 | 5.2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | milligrams per litre | Daily during any Discharge | 16 | 0.11 | 3.27 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | milligrams per litre | Daily during any Discharge | 16 | 1.81 | 8.7 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Oil and Grease | milligrams per litre | Daily during any Discharge | 16 | <1 | 6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | milligrams per litre | Daily during any Discharge | 16 | 0.45 | 0.71 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | Daily during any Discharge | 16 | <1 | 19 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH | pH | Daily during any Discharge | 16 | 6.88 | 9.81 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 2 | Site Description - At the discharge point at UV Disinfection
Site Code 5DE1500
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 October 2020 - 30 September 2021
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Weekly | 52 | <2 | 17 | N/A | N/A | 20 | 4 | N/A | N/A | 30 | 17 | Yes
Faecal Coliforms | colony forming units per 100 mL | Weekly | 52 | <1 | 4400 | N/A | N/A | 200 | 431 | N/A | N/A | N/A | N/A | No
Nitrogen (ammonia) | milligrams per litre | Weekly | 52 | <0.05 | 4.53 | N/A | N/A | 3 | 0.4 | N/A | N/A | N/A | N/A | Yes
Nitrogen (total) | milligrams per litre | Weekly | 52 | 1.3 | 8.29 | N/A | N/A | 15 | 4.2 | N/A | N/A | N/A | N/A | Yes
Nitrate + Nitrite (oxidised nitrogen) | milligrams per litre | Weekly | 52 | 0.33 | 5.04 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Oil and Grease | milligrams per litre | Fortnightly | 26 | <1 | <2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | milligrams per litre | Weekly | 52 | 0.06 | 1.6 | N/A | N/A | 3 | 0.4 | N/A | N/A | N/A | N/A | Yes
Total Suspended Solids | milligrams per litre | Weekly | 52 | <1 | 30 | N/A | N/A | 20 | 5 | N/A | N/A | 30 | 30 | Yes
pH | pH | Weekly | 52 | 6.91 | 7.72 | N/A | N/A | N/A | N/A | N/A | N/A | 6.50 - 8.50 | 6.91-7.72 | Yes
VOLUME MONITORING
Annual Summary
1 October 2020 - 30 September 2021
Monitoring Point |  | Unit of | Sampling | No. of times measured during the year |  |  |  |  | Volume | Within
|  | Measurement | Frequency |  |  | Minimum | Mean | Maximum | Limit | Limits?
Point 1 - At the discharge from the No.2 Maturation Pond |  | kilolitres per day | Daily | 365 |  | 0 | 607 | 46440 | N/A | N/A
Point 2 - At the discharge point at UV Disinfection |  | kilolitres per day | Daily | 365 |  | 1 | 8375 | 12958 | 90000 | Yes