## Shortland
SHORTLAND WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - MAY 2020
|  | Environment Protection Licence No. 1683 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 4 June 2020 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 18 June 2020 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 20 |  | Site Description - Shortland WWTW dechlorination building
Site Code 5SL1810
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 May 2020 to 31 May 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Special Frequency 1 | Include? | 2 | <2 | 2.5 | 2.5 | 3 | N/A | N/A | N/A | N/A | N/A
Chlorine (free residual) | Free Chlorine | milligrams per litre | (mg/L) | Special Frequency 1 | Include? | 2 | <0.10 | 0.175 | 0.175 | 0.25 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Special Frequency 1 | Include? | 2 | ~2 | 11 | 11 | ~20 | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Special Frequency 1 | Include? | 2 | 2.2 | 3.8 | 3.8 | 5.4 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Special Frequency 1 | Include? | 2 | 0.59 | 0.845 | 0.845 | 1.1 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Special Frequency 1 | Include? | 2 | 4.7 | 6.3 | 6.3 | 7.9 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Special Frequency 1 | Include? | 2 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Special Frequency 1 | Include? | 2 | 6.87 | 6.94 | 6.94 | 7.01 | N/A | N/A | 6.5 - 8.5 | 6.87 - 7.01 | Yes
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Special Frequency 1 | Include? | 2 | 0.36 | 0.43 | 0.43 | 0.5 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Special Frequency 1 | Include? | 2 | 2 | 3.5 | 3.5 | 5 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 18 |  | Site Description - Shortland WWTW overflow
Site Code 5OV1800
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 May 2020 to 31 May 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Chlorophyll 'a' | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Daily during any discharge |  | 2 | 3 | 3.5 | 3.5 | 4 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Daily during any discharge |  | 2 | 31000 | 135500 | 135500 | 240000 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Daily during any discharge |  | 2 | 3.5 | 3.6 | 3.6 | 3.7 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Daily during any discharge |  | 2 | 7.28 | 7.315 | 7.315 | 7.35 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Daily during any discharge |  | 2 | <1 | 4 | 4 | 7 | N/A | N/A | N/A | N/A | N/A
VOLUME MONITORING |  |  | 47
Monthly Summary
1 May 2020 to 31 May 2020
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  |  | Volume | Within Limits
|  |  |  | Measurement |  | Frequency |  |  | Maximum | Limit
Point 20 - Shortland WWTW dechlorination building |  |  | 6 | kilolitres per day | 22.859 | Daily | 31 |  | 22859 | 31000 | Yes
Chlorophyll 'a'
Chlorophyll 'a'
Note on D42: awebb: Last row of flow table