## Shortland
SHORTLAND WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - MAY 2021
|  | Environment Protection Licence No. 1683 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 1 June 2021 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 22 June 2021 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 20 |  | Site Description - Shortland WWTW dechlorination building
Site Code 5SL1810
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 May 2021 to 31 May 2021
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Special Frequency 1 | Include? | 1 | 2 | 2 | 2 | 2 | N/A | N/A | N/A | N/A | N/A
Chlorine (free residual) | Free Chlorine | milligrams per litre | (mg/L) | Special Frequency 1 | Include? | 1 | <0.1 | <0.1 | <0.1 | <0.1 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Special Frequency 1 | Include? | 1 | ~2 | ~2 | ~2 | ~2 | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Special Frequency 1 | Include? | 1 | 8.12 | 8.12 | 8.12 | 8.12 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Special Frequency 1 | Include? | 1 | 0.66 | 0.66 | 0.66 | 0.66 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Special Frequency 1 | Include? | 1 | 11.02 | 11.02 | 11.02 | 11.02 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Special Frequency 1 | Include? | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Special Frequency 1 | Include? | 1 | 6.81 | 6.81 | 6.81 | 6.81 | N/A | N/A | 6.5 - 8.5 | 6.81 - 6.81 | Yes
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Special Frequency 1 | Include? | 1 | 0.72 | 0.72 | 0.72 | 0.72 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Special Frequency 1 | Include? | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 18 |  | Site Description - Shortland WWTW overflow
Site Code 5OV1800
[6 empty] | No. of times measured during the month for licence reporting ** | Monthly Summary
1 May 2021 to 31 May 2021
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Chlorophyll 'a' | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Daily during any discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Daily during any discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Daily during any discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Daily during any discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Daily during any discharge |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
** No samples were collected as no discharge occurred during the month
VOLUME MONITORING |  |  | 47
Monthly Summary
1 May 2021 to 31 May 2021
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
|  |  |  | Measurement |  | Frequency | [5 empty] | Limit
Point 20 - Shortland WWTW dechlorination building |  |  | 6 | kilolitres per day | 4.847 | Daily | 31 |  | 0 | 308 | 4847 | 31000 | Yes
Chlorophyll 'a'
Chlorophyll 'a'
Note on D42: awebb: Last row of flow table