## Shortland
SHORTLAND WASTEWATER TREATMENT WORKS - ANNUAL POLLUTION MONITORING SUMMARY - 2019-2020
| Environment Protection Licence No. 1683 |  |  |  | Hunter Water Corporation
| Date Obtained: 1 July 2020 |  |  |  | 36 Honeysuckle Drive
| Date Published: 20 July 2020 |  |  |  | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 20 | Site Description -Shortland WWTW dechlorination building
Site Code 5SL1810
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 July 2019 to 30 June 2020
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Number of measurements | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Special Frequency 1 | 26 | <2 | 41 | 25 | 4 | 60 | 9 | N/A | N/A | N/A | N/A | N/A | Yes
Chlorine (free residual) | milligrams per litre | Special Frequency 1 | 26 | <0.10 | 0.25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | colony forming units per 100 mL | Special Frequency 1 | 26 | ~<1 | 100000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | milligrams per litre | Special Frequency 1 | 26 | 2.2 | 9.3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | Special Frequency 1 | 26 | 0.31 | 2.4 | N/A | N/A | 8 | 2.3 | N/A | N/A | N/A | N/A | N/A | Yes
Nitrogen (total) | milligrams per litre | Special Frequency 1 | 26 | 4.7 | 11.8 | N/A | N/A | 20 | 10.5 | N/A | N/A | N/A | N/A | N/A | Yes
Oil and Grease | milligrams per litre | Special Frequency 1 | 26 | <2 | 4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH | pH | Special Frequency 1 | 26 | 6.39 | 7.15 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 6.5 - 8.5 | 6.39 - 7.15 | No
Phosphorus (total) | milligrams per litre | Special Frequency 1 | 26 | 0.36 | 6.9 | N/A | N/A | 7 | 4.05 | N/A | N/A | N/A | N/A | N/A | Yes
Total Suspended Solids | milligrams per litre | Special Frequency 1 | 26 | <1 | 36 | 40 | 6 | 80 | 11 | N/A | N/A | N/A | N/A | N/A | Yes
EPA Id. No. 18 | Site Description - Overflow structure of the storm storage pond
Site Code 5OV1800
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 July 2019 to 30 June 2020
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Number of measurements | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Daily during any discharge | 17 | <2 | 14 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | colony forming units per 100 mL | Daily during any discharge | 17 | ~720 | 420000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | Daily during any discharge | 17 | 2 | 3.7 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH | pH | Daily during any discharge | 17 | 6.91 | 7.55 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | Daily during any discharge | 17 | <1 | 26 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
VOLUME MONITORING
Annual Summary
1 July 2019 to 30 June 2020
|  |  | Unit of | Sampling | No. of times measured during the year |  |  | Volume | Within
Monitoring Point |  |  | Measurement | Frequency |  |  | Maximum | Limit | Limits?
Point 20 - Dechlorinated Discharge to Hunter River |  |  | kilolitres per day | Daily | 366 |  | 22859 | 31000 | Yes

## Shortland (V2) (hidden)
SHORTLAND WASTEWATER TREATMENT WORKS - ANNUAL POLLUTION MONITORING SUMMARY
| Environment Protection Licence No. 1683 |  |  |  | Hunter Water Corporation
| Date Obtained: 3 July 2017 |  |  |  | 36 Honeysuckle Drive
| Date Published: |  |  |  | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 20 | Site Description -Shortland WWTW dechlorination building
Site Code 5SL1810
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 July 2016 to 5 September 2016
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Number of measurements | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Special Frequency 1 | 8 | <2 | 6 | 25 | 3 | 60 | 3.9 | N/A | N/A | N/A | 80 | 6 | Yes
Faecal Coliforms | colony forming units per 100 mL | Special Frequency 1 | 8 | 2 | 2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | milligrams per litre | Special Frequency 1 | 8 | 4.1 | 8.5 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | Special Frequency 1 | 8 | 0.05 | 3.8 | N/A | N/A | 8 | 1.77 | N/A | N/A | N/A | N/A | N/A | Yes
Oil and Grease | milligrams per litre | Special Frequency 1 | 8 | <2 | <2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH | pH | Special Frequency 1 | 8 | 6.5 | 7.1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 6.5 - 8.5 | 6.5 - 7.1 | Yes
Phosphorus (total) | milligrams per litre | Special Frequency 1 | 8 | 1.8 | 6.5 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | Special Frequency 1 | 8 | <1 | 14 | 40 | 6 | 80 | 10.5 | N/A | N/A | N/A | 100 | 14 | Yes
EPA Id. No. 20 | Site Description -Shortland WWTW dechlorination building
Site Code 5SL1810
|  |  | No. of times measured during the year for licence reporting | Annual Summary
6 September 2016 to 30 June 2017
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Number of measurements | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Special Frequency 1 | 26 | <2 | 5 | 25 | <2 | 60 | 4 | N/A | N/A | N/A | N/A | N/A | Yes
Chlorine (free residual) | milligrams per litre | Special Frequency 1 | 20* | <0.10 | 0.77 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | colony forming units per 100 mL | Special Frequency 1 | 26 | 2 | 3600 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrate + Nitrite (oxidised nitrogen) | milligrams per litre | Special Frequency 1 | 26 | 2.8 | 26.5 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | Special Frequency 1 | 26 | <0.05 | 4.5 | N/A | N/A | 8 | 1.6 | N/A | N/A | N/A | N/A | N/A | Yes
Oil and Grease | milligrams per litre | Special Frequency 1 | 26 | <2 | 3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH | pH | Special Frequency 1 | 26 | 6.56 | 7.12 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 6.50 - 8.50 | 6.56 - 7.12 | Yes
Phosphorus (total) | milligrams per litre | Special Frequency 1 | 26 | 0.72 | 8.5 | N/A | N/A | 7 | 4.3 | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | Special Frequency 1 | 26 | <1 | 26 | 40 | 5 | 80 | 14.5 | N/A | N/A | N/A | N/A | N/A | Yes
* Sample not analysed for Chlorine (free residual) on six occasions
EPA Id. No. 18 | Site Description -Shortland WWTW overflow
Site Code 5OV1800
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 July 2016 to 30 June 2017
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Number of measurements | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Daily during any discharge | 14 | <2 | 17 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | Daily during any discharge | 14 | 0.38 | 4.2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH | pH | Daily during any discharge | 14 | 7.05 | 7.7 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | Daily during any discharge | 14 | <1 | 34 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A