## Tanilba Bay
TANILBA BAY WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - FEBRUARY 2022
|  | Environment Protection Licence No. 4435 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 1 March 2022 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 21 March 2022 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 |  | Site Description - Immediately downstream of the UV disinfection system
Site Code 5SL2900
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2022 to 28 February 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <2 | <2 | <2 | 3 | N/A | N/A | 30 | 3 | Yes
Conductivity | Cond | microsiemens per centimetre | (µS/cm) | Monthly | MONTHLY | 1 | 598 | 598 | 598 | 598 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 0.26 | 0.26 | 0.26 | 0.26 | N/A | N/A | 5 | 0.26 | Yes
Nitrate + Nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 2.08 | 2.08 | 2.08 | 2.08 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 3.68 | 3.68 | 3.68 | 3.68 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Fortnightly | FORTNIGHTLY | 2 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 3.32 | 3.32 | 3.32 | 3.32 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <1 | 3.25 | 3 | 6 | N/A | N/A | 50 | 6 | Yes
pH | pH | pH | pH | Weekly | WEEKLY | 4 | 7.44 | 7.5625 | 7.59 | 7.63 | N/A | N/A | 6.5 - 8.5 | 7.44 - 7.63 | Yes
EPA Id. No. 3 |  | Site Description - Emergency Overflow from Infiltration Pond No.4
Site Code 5OV2900
[6 empty] | No. of times measured during the month for licence reporting # | Monthly Summary
1 February 2022 to 28 February 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Each Overflow Event |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Each Overflow Event |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Each Overflow Event |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Each Overflow Event |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Each Overflow Event |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
# No samples were collected as no discharge occurred during the month
EPA Id. No. 4 |  | Site Description - Groundwater Bore 51
Site Code 54Z2901
|  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2022 to 28 February 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | 4 | Quarterly |  | 1 | 2 | 2 | 2 | 2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | 4 | Quarterly |  | 1 | 309 | 309 | 309 | 309 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL | 4 | Quarterly |  | 1 | ~<1 | ~<1 | ~<1 | ~<1 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | 4 | Quarterly |  | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | 4 | Quarterly |  | 1 | 1.22 | 1.22 | 1.22 | 1.22 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | 4 | Quarterly |  | 1 | 1.65 | 1.65 | 1.65 | 1.65 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | 4 | Quarterly |  | 1 | 5.7 | 5.7 | 5.7 | 5.7 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | 4 | Quarterly |  | 1 | 0.064 | 0.064 | 0.064 | 0.064 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | 4 | Quarterly |  | 1 | 2 | 2 | 2 | 2 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) | 4 | Quarterly |  | 1 | 2.73 | 2.73 | 2.73 | 2.73 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 5 |  | Site Description - Groundwater Bore 151
Site Code 54Z2902
|  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2022 to 28 February 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | 4 | Quarterly |  | 1 | 2 | 2 | 2 | 2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | 4 | Quarterly |  | 1 | 271 | 271 | 271 | 271 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL | 4 | Quarterly |  | 1 | ~<1 | ~<1 | ~<1 | ~<1 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | 4 | Quarterly |  | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | 4 | Quarterly |  | 1 | 0.63 | 0.63 | 0.63 | 0.63 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | 4 | Quarterly |  | 1 | 1.15 | 1.15 | 1.15 | 1.15 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | 4 | Quarterly |  | 1 | 6.57 | 6.57 | 6.57 | 6.57 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | 4 | Quarterly |  | 1 | 0.006 | 0.006 | 0.006 | 0.006 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | 4 | Quarterly |  | 1 | 7 | 7 | 7 | 7 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) | 4 | Quarterly |  | 1 | 3.48 | 3.48 | 3.48 | 3.48 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 6 |  | Site Description - Groundwater Bore 251
Site Code 54Z2903
|  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2022 to 28 February 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | 4 | Quarterly |  | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | 4 | Quarterly |  | 1 | 286 | 286 | 286 | 286 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL | 4 | Quarterly |  | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | 4 | Quarterly |  | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | 4 | Quarterly |  | 1 | 0.7 | 0.7 | 0.7 | 0.7 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | 4 | Quarterly |  | 1 | 1.05 | 1.05 | 1.05 | 1.05 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | 4 | Quarterly |  | 1 | 6.2 | 6.2 | 6.2 | 6.2 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | 4 | Quarterly |  | 1 | 0.01 | 0.01 | 0.01 | 0.01 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | 4 | Quarterly |  | 1 | 9 | 9 | 9 | 9 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) | 4 | Quarterly |  | 1 | 3.42 | 3.42 | 3.42 | 3.42 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 7 |  | Site Description - Groundwater Bore 52
Site Code 54Z2904
|  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2022 to 28 February 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | 4 | Quarterly |  | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | 4 | Quarterly |  | 1 | 291 | 291 | 291 | 291 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL | 4 | Quarterly |  | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | 4 | Quarterly |  | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | 4 | Quarterly |  | 1 | 0.29 | 0.29 | 0.29 | 0.29 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | 4 | Quarterly |  | 1 | 0.65 | 0.65 | 0.65 | 0.65 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | 4 | Quarterly |  | 1 | 6.77 | 6.77 | 6.77 | 6.77 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | 4 | Quarterly |  | 1 | <0.005 | <0.005 | <0.005 | <0.005 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | 4 | Quarterly |  | 1 | 12 | 12 | 12 | 12 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) | 4 | Quarterly |  | 1 | 2.21 | 2.21 | 2.21 | 2.21 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 8 |  | Site Description - Groundwater Bore 152
Site Code 54Z2905
|  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2022 to 28 February 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | 4 | Quarterly |  | 1 | 3 | 3 | 3 | 3 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | 4 | Quarterly |  | 1 | 291 | 291 | 291 | 291 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL | 4 | Quarterly |  | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | 4 | Quarterly |  | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | 4 | Quarterly |  | 1 | 0.17 | 0.17 | 0.17 | 0.17 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | 4 | Quarterly |  | 1 | 0.7 | 0.7 | 0.7 | 0.7 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | 4 | Quarterly |  | 1 | 6.78 | 6.78 | 6.78 | 6.78 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | 4 | Quarterly |  | 1 | <0.005 | <0.005 | <0.005 | <0.005 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | 4 | Quarterly |  | 1 | 6 | 6 | 6 | 6 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) | 4 | Quarterly |  | 1 | 2.31 | 2.31 | 2.31 | 2.31 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 9 |  | Site Description - Groundwater Bore 252
Site Code 54Z2906
|  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2022 to 28 February 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | 4 | Quarterly |  | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | 4 | Quarterly |  | 1 | 275 | 275 | 275 | 275 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL | 4 | Quarterly |  | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | 4 | Quarterly |  | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | 4 | Quarterly |  | 1 | 0.21 | 0.21 | 0.21 | 0.21 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | 4 | Quarterly |  | 1 | 0.55 | 0.55 | 0.55 | 0.55 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | 4 | Quarterly |  | 1 | 6.96 | 6.96 | 6.96 | 6.96 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | 4 | Quarterly |  | 1 | <0.005 | <0.005 | <0.005 | <0.005 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | 4 | Quarterly |  | 1 | 4 | 4 | 4 | 4 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) | 4 | Quarterly |  | 1 | 2.29 | 2.29 | 2.29 | 2.29 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 10 |  | Site Description - Groundwater Bore 53
Site Code 54Z2907
|  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2022 to 28 February 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | 4 | Quarterly |  | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | 4 | Quarterly |  | 1 | 312 | 312 | 312 | 312 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL | 4 | Quarterly |  | 1 | ~<1 | ~<1 | ~<1 | ~<1 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | 4 | Quarterly |  | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | 4 | Quarterly |  | 1 | 0.35 | 0.35 | 0.35 | 0.35 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | 4 | Quarterly |  | 1 | 0.85 | 0.85 | 0.85 | 0.85 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | 4 | Quarterly |  | 1 | 6.76 | 6.76 | 6.76 | 6.76 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | 4 | Quarterly |  | 1 | 0.006 | 0.006 | 0.006 | 0.006 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | 4 | Quarterly |  | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) | 4 | Quarterly |  | 1 | 2.82 | 2.82 | 2.82 | 2.82 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 11 |  | Site Description - Groundwater Bore 153
Site Code 54Z2933
|  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2022 to 28 February 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | 4 | Quarterly |  | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | 4 | Quarterly |  | 1 | 442 | 442 | 442 | 442 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL | 4 | Quarterly |  | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | 4 | Quarterly |  | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | 4 | Quarterly |  | 1 | 0.49 | 0.49 | 0.49 | 0.49 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | 4 | Quarterly |  | 1 | 0.95 | 0.95 | 0.95 | 0.95 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | 4 | Quarterly |  | 1 | 6.78 | 6.78 | 6.78 | 6.78 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | 4 | Quarterly |  | 1 | <0.005 | <0.005 | <0.005 | <0.005 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | 4 | Quarterly |  | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) | 4 | Quarterly |  | 1 | 2.79 | 2.79 | 2.79 | 2.79 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 12 |  | Site Description - Groundwater Bore 253
Site Code 54Z2934
|  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2022 to 28 February 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | 4 | Quarterly |  | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | 4 | Quarterly |  | 1 | 399 | 399 | 399 | 399 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL | 4 | Quarterly |  | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | 4 | Quarterly |  | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | 4 | Quarterly |  | 1 | 0.22 | 0.22 | 0.22 | 0.22 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | 4 | Quarterly |  | 1 | 0.35 | 0.35 | 0.35 | 0.35 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | 4 | Quarterly |  | 1 | 6.28 | 6.28 | 6.28 | 6.28 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | 4 | Quarterly |  | 1 | <0.005 | <0.005 | <0.005 | <0.005 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | 4 | Quarterly |  | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) | 4 | Quarterly |  | 1 | 2.78 | 2.78 | 2.78 | 2.78 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 13 |  | Site Description - Groundwater Bore 54
Site Code 54Z2935
|  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2022 to 28 February 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | 4 | Quarterly |  | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | 4 | Quarterly |  | 1 | 340 | 340 | 340 | 340 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL | 4 | Quarterly |  | 1 | 1 | 1 | 1 | 1 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | 4 | Quarterly |  | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | 4 | Quarterly |  | 1 | 0.67 | 0.67 | 0.67 | 0.67 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | 4 | Quarterly |  | 1 | 0.95 | 0.95 | 0.95 | 0.95 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | 4 | Quarterly |  | 1 | 6.5 | 6.5 | 6.5 | 6.5 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | 4 | Quarterly |  | 1 | 0.03 | 0.03 | 0.03 | 0.03 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | 4 | Quarterly |  | 1 | 2 | 2 | 2 | 2 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) | 4 | Quarterly |  | 1 | 3.84 | 3.84 | 3.84 | 3.84 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 14 |  | Site Description - Groundwater Bore 55
Site Code 54Z2936
|  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2022 to 28 February 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | 4 | Quarterly |  | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | 4 | Quarterly |  | 1 | 107 | 107 | 107 | 107 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL | 4 | Quarterly |  | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | 4 | Quarterly |  | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | 4 | Quarterly |  | 1 | 0.24 | 0.24 | 0.24 | 0.24 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | 4 | Quarterly |  | 1 | 0.35 | 0.35 | 0.35 | 0.35 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | 4 | Quarterly |  | 1 | 6.1 | 6.1 | 6.1 | 6.1 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | 4 | Quarterly |  | 1 | <0.005 | <0.005 | <0.005 | <0.005 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | 4 | Quarterly |  | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) | 4 | Quarterly |  | 1 | 4.04 | 4.04 | 4.04 | 4.04 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 15 |  | Site Description - Groundwater Bore 57
Site Code 54Z2938
|  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2022 to 28 February 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | 4 | Quarterly |  | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | 4 | Quarterly |  | 1 | 312 | 312 | 312 | 312 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL | 4 | Quarterly |  | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | 4 | Quarterly |  | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | 4 | Quarterly |  | 1 | 0.57 | 0.57 | 0.57 | 0.57 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | 4 | Quarterly |  | 1 | 1.15 | 1.15 | 1.15 | 1.15 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | 4 | Quarterly |  | 1 | 6.55 | 6.55 | 6.55 | 6.55 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | 4 | Quarterly |  | 1 | 0.04 | 0.04 | 0.04 | 0.04 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | 4 | Quarterly |  | 1 | 26 | 26 | 26 | 26 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) | 4 | Quarterly |  | 1 | 3.22 | 3.22 | 3.22 | 3.22 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 16 |  | Site Description - Control Bore SK5389
Site Code 54Z3017
|  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2022 to 28 February 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | 4 | Quarterly |  | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | 4 | Quarterly |  | 1 | 155 | 155 | 155 | 155 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL | 4 | Quarterly |  | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | 4 | Quarterly |  | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | 4 | Quarterly |  | 1 | 0.28 | 0.28 | 0.28 | 0.28 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | 4 | Quarterly |  | 1 | 0.25 | 0.25 | 0.25 | 0.25 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | 4 | Quarterly |  | 1 | 5.42 | 5.42 | 5.42 | 5.42 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | 4 | Quarterly |  | 1 | 0.01 | 0.01 | 0.01 | 0.01 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | 4 | Quarterly |  | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) | 4 | Quarterly |  | 1 | 4.82 | 4.82 | 4.82 | 4.82 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 17 |  | Site Description - Infiltration Pond 1
Site Code 54Z3013
[6 empty] | No. of times measured during the month for licence reporting* | Monthly Summary
1 February 2022 to 28 February 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | (µS/cm) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
* Sample not collected as the pond was dry.
EPA Id. No. 18 |  | Site Description - Infiltration Pond 2
Site Code 54Z3014
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2022 to 28 February 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Quarterly |  | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | (µS/cm) | Quarterly |  | 1 | 597 | 597 | 597 | 597 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Quarterly |  | 1 | ~18 | ~18 | ~18 | ~18 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Quarterly |  | 1 | 2.03 | 2.03 | 2.03 | 2.03 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Quarterly |  | 1 | 0.29 | 0.29 | 0.29 | 0.29 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Quarterly |  | 1 | 2.83 | 2.83 | 2.83 | 2.83 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Quarterly |  | 1 | 7.58 | 7.58 | 7.58 | 7.58 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Quarterly |  | 1 | 2.76 | 2.76 | 2.76 | 2.76 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Quarterly |  | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 19 |  | Site Description - Infiltration Pond 3
Site Code 54Z3015
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2022 to 28 February 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Quarterly |  | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | (µS/cm) | Quarterly |  | 1 | 597 | 597 | 597 | 597 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Quarterly |  | 1 | ~18 | ~18 | ~18 | ~18 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Quarterly |  | 1 | 2.14 | 2.14 | 2.14 | 2.14 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Quarterly |  | 1 | 0.23 | 0.23 | 0.23 | 0.23 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Quarterly |  | 1 | 2.84 | 2.84 | 2.84 | 2.84 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Quarterly |  | 1 | 7.62 | 7.62 | 7.62 | 7.62 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Quarterly |  | 1 | 2.64 | 2.64 | 2.64 | 2.64 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Quarterly |  | 1 | 6 | 6 | 6 | 6 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 20 |  | Site Description - Infiltration Pond 4
Site Code 54Z3016
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2022 to 28 February 2022
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Quarterly |  | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | (µS/cm) | Quarterly |  | 1 | 598 | 598 | 598 | 598 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Quarterly |  | 1 | ~100 | ~100 | ~100 | ~100 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Quarterly |  | 1 | 2.09 | 2.09 | 2.09 | 2.09 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Quarterly |  | 1 | 0.25 | 0.25 | 0.25 | 0.25 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Quarterly |  | 1 | 2.79 | 2.79 | 2.79 | 2.79 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Quarterly |  | 1 | 7.58 | 7.58 | 7.58 | 7.58 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Quarterly |  | 1 | 2.72 | 2.72 | 2.72 | 2.72 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Quarterly |  | 1 | 3 | 3 | 3 | 3 | N/A | N/A | N/A | N/A | N/A
Note: For pollutants with less than four samples measured during the monthly period see below for interpretation of summary tables: One required sample for licence reporting: Min, Mean, Median and Max values are all the exact data point Two required samples for licence reporting: Min and Max values are the two exact data points Three required samples for licence reporting: Min, Median and Max values are the three exact data points
VOLUME MONITORING |  |  | 117
Monthly Summary
1 February 2022 to 28 February 2022
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
|  |  |  | Measurement |  | Frequency | [5 empty] | Limit
Point 2 - Effluent Flume Channel |  |  | 4 | kilolitres per day | 2.52 | Daily | 28 |  | 990 | 1707.5 | 2030 | 10000 | Yes
* Sample not collected as the pond was dry.
*Sample not collected as Infiltration Pond 3 was dry.
* Note: Sample could not be collected from Pond 2 as the pond was less than 10% capacity
Note on D348: awebb: Last row of flow table