## Tanilba Bay
TANILBA BAY WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - AUGUST 2026
|  | Environment Protection Licence No. 4435 | [7 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 1 September 2026 | [8 empty] | 36 Honeysuckle Drive
|  | Date Published: 21 September 2026 | [8 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 21 |  | Site Description - Immediately downstream of the UV disinfection system
Site Code 5SL2906
[7 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | (mg/L) | Weekly | WEEKLY | 4 | <2 | <2 | <2 | 2 | N/A | N/A | 20 | 2 | Yes
Conductivity | Cond | microsiemens per centimetre |  | (µS/cm) | Monthly | MONTHLY | 1 | 535 | 535 | 535 | 535 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL |  | CFU/100mL | Weekly | WEEKLY | 4 | ~4 | 9 | 10 | ~12 | N/A | N/A | 600 | ~12 | Yes
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | (mg/L) | Monthly | MONTHLY | 1 | 0.09 | 0.09 | 0.09 | 0.09 | N/A | N/A | 5 | 0.09 | Yes
Nitrate + Nitrite (oxidised nitrogen) | TON | milligrams per litre |  | (mg/L) | Monthly | MONTHLY | 1 | 1.14 | 1.14 | 1.14 | 1.14 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | (mg/L) | Monthly | MONTHLY | 1 | 2.04 | 2.04 | 2.04 | 2.04 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre |  | (mg/L) | Fortnightly | FORTNIGHTLY | 2 | <2 | 2.5 | 2.5 | 3 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | (mg/L) | Monthly | MONTHLY | 1 | 1.72 | 1.72 | 1.72 | 1.72 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | (mg/L) | Weekly | WEEKLY | 4 | 2 | 2.75 | 2.5 | 4 | N/A | N/A | 30 | 4 | Yes
pH | pH | pH |  | pH | Weekly | WEEKLY | 4 | 7.46 | 7.52 | 7.5 | 7.62 | N/A | N/A | 6.5 - 8.5 | 7.46 - 7.62 | Yes
EPA Id. No. 3 |  | Site Description - Emergency Overflow from Infiltration Pond No.4
Site Code 5OV2900
[7 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | (mg/L) | Each Overflow Event |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL |  | CFU/100mL | Each Overflow Event |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre |  | (mg/L) | Each Overflow Event |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | (mg/L) | Each Overflow Event |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH |  | pH | Each Overflow Event |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
# No samples were collected as no discharge occurred during the month
EPA Id. No. 4 |  | Site Description - Groundwater Bore 51
Site Code 54Z2901
|  |  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 11 | 11 | 11 | 11 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre |  | 4 | Quarterly | Compliance | 1 | 208 | 208 | 208 | 208 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL |  | 4 | Quarterly | Compliance | 1 | <10 | <10 | <10 | <10 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.3 | 0.3 | 0.3 | 0.3 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 1.45 | 1.45 | 1.45 | 1.45 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH |  | 4 | Quarterly | Compliance | 1 | 5.24 | 5.24 | 5.24 | 5.24 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.019 | 0.019 | 0.019 | 0.019 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 6 | 6 | 6 | 6 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) |  | 4 | Quarterly | Compliance | 1 | 2.43 | 2.43 | 2.43 | 2.43 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 5 |  | Site Description - Groundwater Bore 151
Site Code 54Z2902
|  |  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 5 | 5 | 5 | 5 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre |  | 4 | Quarterly | Compliance | 1 | 507 | 507 | 507 | 507 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL |  | 4 | Quarterly | Compliance | 1 | 12000 | 12000 | 12000 | 12000 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.14 | 0.14 | 0.14 | 0.14 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.3 | 0.3 | 0.3 | 0.3 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.84 | 0.84 | 0.84 | 0.84 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH |  | 4 | Quarterly | Compliance | 1 | 6.5 | 6.5 | 6.5 | 6.5 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.04 | 0.04 | 0.04 | 0.04 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 43 | 43 | 43 | 43 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) |  | 4 | Quarterly | Compliance | 1 | 3.68 | 3.68 | 3.68 | 3.68 | N/A | N/A | N/A | N/A | N/A
31
EPA Id. No. 6 |  | Site Description - Groundwater Bore 251
Site Code 54Z2903
|  |  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre |  | 4 | Quarterly | Compliance | 1 | 386 | 386 | 386 | 386 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL |  | 4 | Quarterly | Compliance | 1 | ~1 | ~1 | ~1 | ~1 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.07 | 0.07 | 0.07 | 0.07 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.08 | 0.08 | 0.08 | 0.08 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.37 | 0.37 | 0.37 | 0.37 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH |  | 4 | Quarterly | Compliance | 1 | 6.99 | 6.99 | 6.99 | 6.99 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.008 | 0.008 | 0.008 | 0.008 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 2 | 2 | 2 | 2 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) |  | 4 | Quarterly | Compliance | 1 | 3.52 | 3.52 | 3.52 | 3.52 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 7 |  | Site Description - Groundwater Bore 52
Site Code 54Z2904
|  |  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 3 | 3 | 3 | 3 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre |  | 4 | Quarterly | Compliance | 1 | 217 | 217 | 217 | 217 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL |  | 4 | Quarterly | Compliance | 1 | ~4 | ~4 | ~4 | ~4 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 1.12 | 1.12 | 1.12 | 1.12 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 1.35 | 1.35 | 1.35 | 1.35 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH |  | 4 | Quarterly | Compliance | 1 | 5.82 | 5.82 | 5.82 | 5.82 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.01 | 0.01 | 0.01 | 0.01 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 8 | 8 | 8 | 8 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) |  | 4 | Quarterly | Compliance | 1 | 2.31 | 2.31 | 2.31 | 2.31 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 8 |  | Site Description - Groundwater Bore 152
Site Code 54Z2905
|  |  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 3 | 3 | 3 | 3 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre |  | 4 | Quarterly | Compliance | 1 | 636 | 636 | 636 | 636 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL |  | 4 | Quarterly | Compliance | 1 | ~<1 | ~<1 | ~<1 | ~<1 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.24 | 0.24 | 0.24 | 0.24 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.65 | 0.65 | 0.65 | 0.65 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH |  | 4 | Quarterly | Compliance | 1 | 6.67 | 6.67 | 6.67 | 6.67 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.037 | 0.037 | 0.037 | 0.037 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 21 | 21 | 21 | 21 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) |  | 4 | Quarterly | Compliance | 1 | 2.01 | 2.01 | 2.01 | 2.01 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 9 |  | Site Description - Groundwater Bore 252
Site Code 54Z2906
|  |  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 4 | 4 | 4 | 4 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre |  | 4 | Quarterly | Compliance | 1 | 436 | 436 | 436 | 436 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL |  | 4 | Quarterly | Compliance | 1 | ~<1 | ~<1 | ~<1 | ~<1 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.08 | 0.08 | 0.08 | 0.08 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.08 | 0.08 | 0.08 | 0.08 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.58 | 0.58 | 0.58 | 0.58 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH |  | 4 | Quarterly | Compliance | 1 | 6.82 | 6.82 | 6.82 | 6.82 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.027 | 0.027 | 0.027 | 0.027 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 41 | 41 | 41 | 41 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) |  | 4 | Quarterly | Compliance | 1 | 2.09 | 2.09 | 2.09 | 2.09 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 10 |  | Site Description - Groundwater Bore 53
Site Code 54Z2907
|  |  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre |  | 4 | Quarterly | Compliance | 1 | 487 | 487 | 487 | 487 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL |  | 4 | Quarterly | Compliance | 1 | <10 | <10 | <10 | <10 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.62 | 0.62 | 0.62 | 0.62 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.43 | 0.43 | 0.43 | 0.43 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 1.52 | 1.52 | 1.52 | 1.52 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH |  | 4 | Quarterly | Compliance | 1 | 6.97 | 6.97 | 6.97 | 6.97 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.006 | 0.006 | 0.006 | 0.006 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 7 | 7 | 7 | 7 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) |  | 4 | Quarterly | Compliance | 1 | 2.52 | 2.52 | 2.52 | 2.52 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 11 |  | Site Description - Groundwater Bore 153
Site Code 54Z2933
|  |  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 4 | 4 | 4 | 4 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre |  | 4 | Quarterly | Compliance | 1 | 543 | 543 | 543 | 543 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL |  | 4 | Quarterly | Compliance | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 1.41 | 1.41 | 1.41 | 1.41 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 2.05 | 2.05 | 2.05 | 2.05 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH |  | 4 | Quarterly | Compliance | 1 | 6.89 | 6.89 | 6.89 | 6.89 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.026 | 0.026 | 0.026 | 0.026 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) |  | 4 | Quarterly | Compliance | 1 | 2.49 | 2.49 | 2.49 | 2.49 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 12 |  | Site Description - Groundwater Bore 253
Site Code 54Z2934
|  |  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 4 | 4 | 4 | 4 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre |  | 4 | Quarterly | Compliance | 1 | 415 | 415 | 415 | 415 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL |  | 4 | Quarterly | Compliance | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.18 | 0.18 | 0.18 | 0.18 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.78 | 0.78 | 0.78 | 0.78 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH |  | 4 | Quarterly | Compliance | 1 | 6.75 | 6.75 | 6.75 | 6.75 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.148 | 0.148 | 0.148 | 0.148 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 48 | 48 | 48 | 48 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) |  | 4 | Quarterly | Compliance | 1 | 2.48 | 2.48 | 2.48 | 2.48 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 13 |  | Site Description - Groundwater Bore 54
Site Code 54Z2935
|  |  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 4 | 4 | 4 | 4 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre |  | 4 | Quarterly | Compliance | 1 | 382 | 382 | 382 | 382 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL |  | 4 | Quarterly | Compliance | 1 | ~1 | ~1 | ~1 | ~1 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 1 | 1 | 1 | 1 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 1.55 | 1.55 | 1.55 | 1.55 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH |  | 4 | Quarterly | Compliance | 1 | 6.71 | 6.71 | 6.71 | 6.71 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.013 | 0.013 | 0.013 | 0.013 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 8 | 8 | 8 | 8 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) |  | 4 | Quarterly | Compliance | 1 | 3.44 | 3.44 | 3.44 | 3.44 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 14 |  | Site Description - Groundwater Bore 55
Site Code 54Z2936
|  |  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre |  | 4 | Quarterly | Compliance | 1 | 208 | 208 | 208 | 208 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL |  | 4 | Quarterly | Compliance | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.22 | 0.22 | 0.22 | 0.22 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.07 | 0.07 | 0.07 | 0.07 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.82 | 0.82 | 0.82 | 0.82 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH |  | 4 | Quarterly | Compliance | 1 | 6.57 | 6.57 | 6.57 | 6.57 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.056 | 0.056 | 0.056 | 0.056 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) |  | 4 | Quarterly | Compliance | 1 | 4.04 | 4.04 | 4.04 | 4.04 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 15 |  | Site Description - Groundwater Bore 57
Site Code 54Z2938
|  |  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 50 | 50 | 50 | 50 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre |  | 4 | Quarterly | Compliance | 1 | 715 | 715 | 715 | 715 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL |  | 4 | Quarterly | Compliance | 1 | ~<10 | ~<10 | ~<10 | ~<10 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 3.49 | 3.49 | 3.49 | 3.49 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 4.85 | 4.85 | 4.85 | 4.85 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH |  | 4 | Quarterly | Compliance | 1 | 6.68 | 6.68 | 6.68 | 6.68 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.413 | 0.413 | 0.413 | 0.413 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 181 | 181 | 181 | 181 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) |  | 4 | Quarterly | Compliance | 1 | 1.52 | 1.52 | 1.52 | 1.52 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 16 |  | Site Description - Control Bore SK5389
Site Code 54Z3017
|  |  |  | No. of times measured during the month for licence reporting |  |  | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 3 | 3 | 3 | 3 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre |  | 4 | Quarterly | Compliance | 1 | 170 | 170 | 170 | 170 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC | colony forming units per 100 mL |  | 4 | Quarterly | Compliance | 1 | <10 | <10 | <10 | <10 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.05 | 0.05 | 0.05 | 0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.14 | 0.14 | 0.14 | 0.14 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.45 | 0.45 | 0.45 | 0.45 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH |  | 4 | Quarterly | Compliance | 1 | 5.21 | 5.21 | 5.21 | 5.21 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 0.114 | 0.114 | 0.114 | 0.114 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | 4 | Quarterly | Compliance | 1 | 117 | 117 | 117 | 117 | N/A | N/A | N/A | N/A | N/A
Depth | Depth | metres (Australian Height Datum) |  | 4 | Quarterly | Compliance | 1 | 4.52 | 4.52 | 4.52 | 4.52 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 17 |  | Site Description - Infiltration Pond 1
Site Code 54Z3013
[7 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | (mg/L) | Quarterly | Compliance | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre |  | (µS/cm) | Quarterly | Compliance | 1 | 538 | 538 | 538 | 538 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL |  | CFU/100mL | Quarterly | Compliance | 1 | ~20 | ~20 | ~20 | ~20 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre |  | (mg/L) | Quarterly | Compliance | 1 | 1.05 | 1.05 | 1.05 | 1.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | (mg/L) | Quarterly | Compliance | 1 | 0.1 | 0.1 | 0.1 | 0.1 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | (mg/L) | Quarterly | Compliance | 1 | 1.75 | 1.75 | 1.75 | 1.75 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH |  | pH | Quarterly | Compliance | 1 | 7.4 | 7.4 | 7.4 | 7.4 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | (mg/L) | Quarterly | Compliance | 1 | 1.31 | 1.31 | 1.31 | 1.31 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | (mg/L) | Quarterly | Compliance | 1 | 1 | 1 | 1 | 1 | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 18 |  | Site Description - Infiltration Pond 2
Site Code 54Z3014
[7 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | (mg/L) | Quarterly | Compliance | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre |  | (µS/cm) | Quarterly | Compliance | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL |  | CFU/100mL | Quarterly | Compliance | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre |  | (mg/L) | Quarterly | Compliance | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | (mg/L) | Quarterly | Compliance | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | (mg/L) | Quarterly | Compliance | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH |  | pH | Quarterly | Compliance | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | (mg/L) | Quarterly | Compliance | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | (mg/L) | Quarterly | Compliance | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
* Sample not collected as the pond was dry.
EPA Id. No. 19 |  | Site Description - Infiltration Pond 3
Site Code 54Z3015
[7 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | (mg/L) | Quarterly | Compliance | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre |  | (µS/cm) | Quarterly | Compliance | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL |  | CFU/100mL | Quarterly | Compliance | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre |  | (mg/L) | Quarterly | Compliance | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | (mg/L) | Quarterly | Compliance | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | (mg/L) | Quarterly | Compliance | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH |  | pH | Quarterly | Compliance | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | (mg/L) | Quarterly | Compliance | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | (mg/L) | Quarterly | Compliance | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
* Sample not collected as the pond was dry.
EPA Id. No. 20 |  | Site Description - Infiltration Pond 4
Site Code 54Z3016
[7 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 August 2026 to 31 August 2026
|  | Unit of |  |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre |  | (mg/L) | Quarterly | Compliance | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre |  | (µS/cm) | Quarterly | Compliance | 1 | 544 | 544 | 544 | 544 | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL |  | CFU/100mL | Quarterly | Compliance | 1 | ~100 | ~100 | ~100 | ~100 | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre |  | (mg/L) | Quarterly | Compliance | 1 | 0.65 | 0.65 | 0.65 | 0.65 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre |  | (mg/L) | Quarterly | Compliance | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre |  | (mg/L) | Quarterly | Compliance | 1 | 1.15 | 1.15 | 1.15 | 1.15 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH |  | pH | Quarterly | Compliance | 1 | 7.56 | 7.56 | 7.56 | 7.56 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre |  | (mg/L) | Quarterly | Compliance | 1 | 1.41 | 1.41 | 1.41 | 1.41 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre |  | (mg/L) | Quarterly | Compliance | 1 | <1 | <1 | <1 | <1 | N/A | N/A | N/A | N/A | N/A
Note: For pollutants with less than four samples measured during the monthly period see below for interpretation of summary tables: One required sample for licence reporting: Min, Mean, Median and Max values are all the exact data point Two required samples for licence reporting: Min and Max values are the two exact data points Three required samples for licence reporting: Min, Median and Max values are the three exact data points
VOLUME MONITORING |  |  |  | 356
Monthly Summary
1 August 2026 to 31 August 2026
Monitoring Point |  |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
[5 empty] | Measurement |  | Frequency | [5 empty] | Limit
Point 2 - Effluent Flume Channel |  |  | 2 | 4 | kilolitres per day | 2.52 | Continuous | 31 |  | 835 | 1516 | 2580 | 15500 | Yes
Point 22 - UV system feed pump station |  |  | 0 | 7 | kilolitres per day | 2.52 | Continuous | 31 |  | 766 | 1376 | 1734 | N/A | Yes
Point 23 - Inlet flow meter |  |  | 2 | 3 | kilolitres per day | 2.52 | Continuous | 31 |  | 1250 | 1327.4194 | 1420 | N/A | Yes
Note on E349: awebb: Last row of flow table